## GES_VLS_CUE
Sequencing | Pump Size ID | Pump Size | Curve | Max flow @ max speed (gpm), 1 pump | Max Branch Flow | Max Header Flow | Number of Active Pumps | Number of Backup Pumps | Number of Total Pumps | Cost Group | Cost Group Type | Suction | Discharge | Branch Minimum | Branch Maximum | Branch Range | Header Minimum | Header Maximum | Header Range | Weird | Flow Corrected
1 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 241.807 | 2 | 0 | 2 | A | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
2 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 268.3898 | 2 | 0 | 2 | A | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
3 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 293.4682 | 2 | 0 | 2 | A | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
4 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 308 | 2 | 0 | 2 | A | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
5 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 158 | 2 | 0 | 2 | A | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
6 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 339.9431 | 2 | 0 | 2 | A | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
7 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 383.8779 | 2 | 0 | 2 | A | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
8 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 452.6514 | 2 | 0 | 2 | A | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
9 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 248.1382 | 2 | 0 | 2 | A | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
10 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 380.3819 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
11 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 428.1031 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
12 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 499.7046 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
13 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 487.9832 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
14 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 256.3121 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
15 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 305.9 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
16 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 336.461 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
17 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 369.056 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
18 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 382.64 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
19 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 180.6582 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
20 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 190.44 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
21 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 352.2451 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
22 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 400.7361 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
23 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 465.1173 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
24 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 465.1173 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
25 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 222.8964 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
26 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 237.2737 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
27 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 410.7272 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
28 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 471.2947 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
29 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 514.8 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
30 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 554.9253 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
31 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 600 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
32 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 600 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
33 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 272.2118 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
34 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 325.274 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
35 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 330.6542 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
36 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 543.9066 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
37 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 618.679 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
38 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 682.5695 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
39 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 761.716 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
40 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 810.2297 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
41 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 813.7556 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
42 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 308.4583 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
43 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 411.7298 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
44 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 455.5833 | 2 | 0 | 2 | A | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
45 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 589.1251 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
46 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 711.7636 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
47 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 830.5515 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
48 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 898.2801 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
49 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 445.8531 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
50 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 679.2659 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
51 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 768.1804 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
52 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 849.1072 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
53 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 982.7205 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
54 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 1103.4836 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
55 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 1146.1024 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
56 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 359.9621 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 4 | HeaderMin_3HeaderMax_4
57 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 475.8063 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
58 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 568.7735 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
59 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 521.17 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
60 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 546.5679 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
61 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 661.9944 | 2 | 0 | 2 | A | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
62 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 1049.5105 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
63 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 1069.8809 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
64 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 1147.8898 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
65 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 1199.4453 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
66 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 1024.7846 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
67 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 1147.6336 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
68 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 1260.3334 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
69 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 1363.39 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 8 | HeaderMin_4HeaderMax_8
70 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 484.1403 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
71 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 583.2733 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
72 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 580.9873 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
73 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 701.3387 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
74 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 750.9605 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
75 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 805.1276 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
76 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 854.771 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
77 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 860.1783 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
78 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 907.68 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
79 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 721.4409 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
80 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 782.7393 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
81 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 889.0754 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
82 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 911.1855 | 2 | 0 | 2 | A | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
83 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 1097.6931 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
84 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 1257.751 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
85 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 1366.9992 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
86 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 1468.4128 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
87 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 1579.5988 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
88 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 721.68 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 6 | HeaderMin_5HeaderMax_6
89 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 854.8766 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6 | Yes | Yes
90 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 1827.6287 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
91 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 1938.8074 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
92 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 2030.6859 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 5 | HeaderMin_5HeaderMax_5
93 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 2103.7154 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 6 | HeaderMin_5HeaderMax_6
94 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 2254.1875 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
95 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 913.1549 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
96 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 1016.1596 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
97 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 1069.8887 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
98 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 1137.64 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
99 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 1770.1484 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
100 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 1825.2504 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
101 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 1910.0257 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
102 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 2049.6538 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
103 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 2233.1676 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
104 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 932.5363 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
105 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 1019.5003 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
106 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 1086.9406 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
107 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 1215.4911 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
108 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 1335.8 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
109 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 1465.6 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
110 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 1549.2 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
111 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 1627 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
112 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 1232.6769 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
113 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 1415.1811 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
114 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 1573.6198 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
115 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 1651 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
116 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 1513.6 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
117 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 1661 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
118 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 1746.6 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
119 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 1278.3144 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
120 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 1589.8266 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
121 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 1764.6841 | 2 | 0 | 2 | A | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
122 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 1871.8526 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
123 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 2272.5482 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
124 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 2665.9362 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
125 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 3056.707 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
126 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 1252.6919 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
127 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 1529.9399 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
128 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 1364.0961 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
129 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 1605.5841 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
130 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 1865.8335 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
131 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 2000.0002 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
132 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 1506.4926 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
133 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 1640.8858 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
134 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 1906.6342 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
135 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 2059.5169 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
136 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 2660.6874 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
137 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 2757.0426 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
138 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 2935.9018 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
139 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 1689.7279 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
140 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 1964.7052 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
141 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 2209.7222 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
142 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 2428.8514 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
143 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 2767.3715 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
144 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 3102.4196 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
145 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 3329.3491 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 12 | HeaderMin_6HeaderMax_12
146 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 1681.5751 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
147 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 1990.9502 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
148 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 2187.3397 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
149 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 2289.7092 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
150 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 2409.0002 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
151 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 2505 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
152 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 1296.767 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
153 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 1640.7178 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
154 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 1882.0704 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
155 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 2090.6314 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
156 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 2273.0192 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
157 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 2471.866 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
158 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 2458.0014 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
159 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 2607.8655 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
160 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 2807.748 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
161 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 2968.6376 | 2 | 0 | 2 | A | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
162 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 2343.8131 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 10 | HeaderMin_8HeaderMax_10
163 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 2633.8694 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
164 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 2908.4756 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
165 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 3137.4434 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
166 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 2829.7672 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
167 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 3046.7486 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
168 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 3250.2342 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
169 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 3514.5593 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
170 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 3693.7017 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
171 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 3829.162 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
172 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 3268.7658 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
173 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 3830.5476 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
174 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 4330.5437 | 2 | 0 | 2 | A | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
175 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 3828.2938 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
176 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 4035.9748 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
177 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 4283.199 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
178 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 4581.157 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
179 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 3454.9903 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 12 | HeaderMin_10HeaderMax_12
180 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 3653.3965 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
181 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 4006.7112 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
182 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 4374.3972 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
183 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 4587.3477 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
184 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 4844.5968 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
185 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 5094.7228 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 16 | HeaderMin_10HeaderMax_16
186 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 5906.1056 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
187 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 6441.9215 | 2 | 0 | 2 | A | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
188 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 7159.7593 | 2 | 0 | 2 | A | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
189 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 7853.7497 | 2 | 0 | 2 | A | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
190 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 8256.5567 | 2 | 0 | 2 | A | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
191 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 362.7105 | 3 | 0 | 3 | B | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
192 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 402.5848 | 3 | 0 | 3 | B | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
193 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 440.2024 | 3 | 0 | 3 | B | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
194 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 462 | 3 | 0 | 3 | B | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
195 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 237 | 3 | 0 | 3 | B | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
196 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 509.9146 | 3 | 0 | 3 | B | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
197 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 575.8169 | 3 | 0 | 3 | B | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
198 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 678.977 | 3 | 0 | 3 | B | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
199 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 372.2073 | 3 | 0 | 3 | B | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
200 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 570.5729 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
201 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 642.1546 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
202 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 749.5569 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
203 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 731.9747 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
204 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 384.4681 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
205 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 458.85 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
206 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 504.6915 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
207 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 553.584 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
208 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 573.96 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
209 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 270.9873 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
210 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 285.66 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
211 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 528.3676 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
212 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 601.1041 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
213 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 697.6759 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
214 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 697.6759 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
215 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 334.3446 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
216 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 355.9106 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
217 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 616.0908 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
218 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 706.9421 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
219 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 772.2001 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
220 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 832.388 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
221 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 900 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
222 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 900 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
223 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 408.3177 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
224 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 487.911 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
225 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 495.9813 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
226 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 815.8599 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
227 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 928.0185 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
228 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 1023.8543 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
229 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 1142.5741 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
230 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 1215.3446 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
231 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 1220.6335 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
232 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 462.6875 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
233 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 617.5946 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
234 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 683.3749 | 3 | 0 | 3 | B | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
235 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 883.6876 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
236 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 1067.6453 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
237 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 1245.8272 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
238 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 1347.4201 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
239 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 668.7796 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
240 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 1018.8988 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
241 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 1152.2706 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
242 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 1273.6608 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
243 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 1474.0808 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
244 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 1655.2254 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
245 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 1719.1537 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
246 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 539.9431 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 5 | HeaderMin_3HeaderMax_5
247 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 713.7094 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
248 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 853.1603 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
249 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 781.755 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
250 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 819.8518 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
251 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 992.9917 | 3 | 0 | 3 | B | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
252 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 1574.2657 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
253 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 1604.8213 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
254 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 1721.8346 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
255 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 1799.168 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
256 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 1537.1769 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
257 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 1721.4503 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
258 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 1890.5 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
259 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 2045.085 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 10 | HeaderMin_4HeaderMax_10
260 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 726.2105 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
261 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 874.91 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
262 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 871.4809 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
263 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 1052.008 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
264 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 1126.4408 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
265 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 1207.6913 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
266 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 1282.1565 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
267 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 1290.2674 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
268 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 1361.52 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
269 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 1082.1614 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
270 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 1174.1089 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
271 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 1333.6131 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
272 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 1366.7783 | 3 | 0 | 3 | B | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
273 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 1646.5396 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
274 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 1886.6265 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
275 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 2050.4988 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
276 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 2202.6191 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
277 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 2369.3983 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
278 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 1082.52 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 8 | HeaderMin_5HeaderMax_8
279 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 1282.3149 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8 | Yes | Yes
280 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 2741.443 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
281 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 2908.2111 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
282 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 3046.0289 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
283 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 3155.5731 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
284 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 3381.2812 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
285 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 1369.7324 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
286 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 1524.2394 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
287 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 1604.833 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
288 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 1706.46 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
289 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 2655.2225 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
290 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 2737.8756 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
291 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 2865.0386 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
292 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 3074.4806 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
293 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 3349.7514 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
294 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 1398.8044 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
295 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 1529.2504 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
296 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 1630.411 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
297 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 1823.2366 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
298 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 2003.7 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
299 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 2198.4 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
300 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 2323.8 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
301 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 2440.5 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
302 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 1849.0154 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
303 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 2122.7716 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
304 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 2360.4297 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
305 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 2476.5 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
306 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 2270.4 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
307 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 2491.5 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
308 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 2619.9 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
309 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 1917.4715 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
310 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 2384.7399 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
311 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 2647.0261 | 3 | 0 | 3 | B | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
312 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 2807.7789 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
313 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 3408.8222 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
314 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 3998.9043 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
315 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 4585.0605 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
316 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 1879.0379 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 10 | HeaderMin_6HeaderMax_10
317 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 2294.9098 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
318 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 2046.1442 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
319 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 2408.3762 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
320 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 2798.7502 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
321 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 3000.0002 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
322 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 2259.739 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
323 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 2461.3287 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
324 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 2859.9513 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
325 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 3089.2754 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
326 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 3991.0312 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
327 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 4135.5639 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
328 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 4403.8528 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
329 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 2534.5919 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
330 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 2947.0578 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
331 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 3314.5834 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
332 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 3643.277 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
333 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 4151.0572 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
334 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 4653.6293 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
335 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 4994.0237 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 16 | HeaderMin_6HeaderMax_16
336 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 2522.3627 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
337 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 2986.4252 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
338 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 3281.0095 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
339 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 3434.5638 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
340 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 3613.5003 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
341 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 3757.5 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
342 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 1945.1505 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 10 | HeaderMin_6HeaderMax_10
343 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 2461.0767 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
344 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 2823.1056 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
345 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 3135.947 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
346 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 3409.5287 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
347 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 3707.799 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
348 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 3687.0022 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
349 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 3911.7983 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
350 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 4211.6221 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
351 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 4452.9564 | 3 | 0 | 3 | B | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
352 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 3515.7196 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
353 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 3950.8041 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 14 | HeaderMin_8HeaderMax_14
354 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 4362.7133 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
355 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 4706.1651 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
356 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 4244.6507 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 14 | HeaderMin_8HeaderMax_14
357 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 4570.123 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
358 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 4875.3512 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
359 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 5271.8389 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
360 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 5540.5526 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
361 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 5743.743 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
362 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 4903.1487 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
363 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 5745.8213 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
364 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 6495.8155 | 3 | 0 | 3 | B | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
365 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 5742.4408 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
366 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 6053.9622 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
367 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 6424.7985 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
368 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 6871.7355 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
369 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 5182.4854 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
370 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 5480.0947 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
371 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 6010.0669 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
372 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 6561.5959 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
373 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 6881.0216 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
374 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 7266.8952 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
375 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 7642.0842 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 20 | HeaderMin_10HeaderMax_20
376 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 8859.1584 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
377 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 9662.8822 | 3 | 0 | 3 | B | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
378 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 10739.639 | 3 | 0 | 3 | B | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
379 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 11780.6245 | 3 | 0 | 3 | B | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
380 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 12384.8351 | 3 | 0 | 3 | B | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
381 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 483.6139 | 4 | 0 | 4 | C | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
382 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 536.7797 | 4 | 0 | 4 | C | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
383 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 586.9365 | 4 | 0 | 4 | C | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
384 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 616 | 4 | 0 | 4 | C | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
385 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 316 | 4 | 0 | 4 | C | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
386 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 679.8862 | 4 | 0 | 4 | C | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
387 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 767.7559 | 4 | 0 | 4 | C | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
388 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 905.3027 | 4 | 0 | 4 | C | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
389 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 496.2764 | 4 | 0 | 4 | C | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
390 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 760.7639 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
391 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 856.2061 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
392 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 999.4092 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
393 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 975.9663 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
394 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 512.6241 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
395 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 611.8001 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
396 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 672.9221 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
397 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 738.1121 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
398 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 765.2801 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
399 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 361.3164 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
400 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 380.88 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
401 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 704.4902 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
402 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 801.4722 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
403 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 930.2345 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
404 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 930.2345 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
405 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 445.7928 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
406 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 474.5474 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
407 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 821.4543 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
408 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 942.5895 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
409 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 1029.6001 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
410 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 1109.8506 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
411 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 1200 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
412 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 1200 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
413 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 544.4236 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
414 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 650.548 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
415 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 661.3083 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
416 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 1087.8131 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
417 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 1237.358 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
418 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 1365.139 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
419 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 1523.4321 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
420 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 1620.4594 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 10 | HeaderMin_2.5HeaderMax_10
421 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 1627.5113 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 10 | HeaderMin_2.5HeaderMax_10
422 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 616.9167 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
423 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 823.4595 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
424 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 911.1665 | 4 | 0 | 4 | C | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
425 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 1178.2501 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
426 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 1423.5271 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
427 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 1661.103 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
428 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 1796.5602 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
429 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 891.7062 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
430 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 1358.5317 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
431 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 1536.3608 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
432 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 1698.2144 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
433 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 1965.4411 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
434 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 2206.9672 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
435 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 2292.2049 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
436 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 719.9241 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 6 | HeaderMin_3HeaderMax_6
437 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 951.6126 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
438 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 1137.547 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
439 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 1042.34 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
440 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 1093.1357 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
441 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 1323.9889 | 4 | 0 | 4 | C | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
442 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 2099.021 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
443 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 2139.7617 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
444 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 2295.7795 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
445 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 2398.8907 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
446 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 2049.5692 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
447 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 2295.2671 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
448 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 2520.6667 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 12 | HeaderMin_4HeaderMax_12
449 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 2726.78 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 12 | HeaderMin_4HeaderMax_12
450 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 968.2806 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
451 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 1166.5466 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
452 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 1161.9746 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
453 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 1402.6774 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
454 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 1501.921 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
455 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 1610.2551 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
456 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 1709.542 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
457 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 1720.3565 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
458 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 1815.36 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
459 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 1442.8819 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
460 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 1565.4785 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
461 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 1778.1508 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
462 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 1822.371 | 4 | 0 | 4 | C | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
463 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 2195.3862 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
464 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 2515.502 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 12 | HeaderMin_5HeaderMax_12
465 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 2733.9985 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
466 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 2936.8255 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
467 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 3159.1977 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
468 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 1443.36 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 8 | HeaderMin_5HeaderMax_8
469 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 1709.7532 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10 | Yes | Yes
470 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 3655.2573 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 14 | HeaderMin_5HeaderMax_14
471 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 3877.6149 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 14 | HeaderMin_5HeaderMax_14
472 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 4061.3719 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 14 | HeaderMin_5HeaderMax_14
473 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 4207.4307 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 14 | HeaderMin_5HeaderMax_14
474 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 4508.3749 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 16 | HeaderMin_5HeaderMax_16
475 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 1826.3098 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
476 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 2032.3192 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
477 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 2139.7774 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
478 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 2275.28 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
479 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 3540.2967 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
480 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 3650.5009 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 14 | HeaderMin_5HeaderMax_14
481 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 3820.0514 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 14 | HeaderMin_5HeaderMax_14
482 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 4099.3075 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 14 | HeaderMin_5HeaderMax_14
483 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 4466.3352 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 16 | HeaderMin_5HeaderMax_16
484 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 1865.0725 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
485 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 2039.0006 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
486 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 2173.8813 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
487 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 2430.9822 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
488 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 2671.6 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
489 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 2931.2 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
490 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 3098.4 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
491 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 3254 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
492 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 2465.3539 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
493 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 2830.3621 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
494 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 3147.2397 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
495 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 3302 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
496 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 3027.2 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
497 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 3322 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
498 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 3493.2 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
499 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 2556.6287 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 12 | HeaderMin_5HeaderMax_12
500 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 3179.6532 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
501 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 3529.3682 | 4 | 0 | 4 | C | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
502 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 3743.7052 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 14 | HeaderMin_6HeaderMax_14
503 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 4545.0963 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
504 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 5331.8724 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
505 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 6113.414 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 18 | HeaderMin_6HeaderMax_18
506 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 2505.3838 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 12 | HeaderMin_6HeaderMax_12
507 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 3059.8797 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
508 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 2728.1922 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
509 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 3211.1683 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
510 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 3731.667 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 14 | HeaderMin_6HeaderMax_14
511 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 4000.0003 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
512 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 3012.9853 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
513 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 3281.7717 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
514 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 3813.2684 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
515 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 4119.0339 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
516 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 5321.3749 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
517 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 5514.0852 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
518 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 5871.8037 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 18 | HeaderMin_6HeaderMax_18
519 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 3379.4558 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
520 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 3929.4104 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
521 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 4419.4445 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
522 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 4857.7027 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
523 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 5534.743 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
524 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 6204.8391 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 18 | HeaderMin_6HeaderMax_18
525 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 6658.6983 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 18 | HeaderMin_6HeaderMax_18
526 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 3363.1503 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
527 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 3981.9003 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
528 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 4374.6794 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
529 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 4579.4184 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
530 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 4818.0004 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
531 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 5010 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
532 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 2593.534 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 12 | HeaderMin_6HeaderMax_12
533 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 3281.4355 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
534 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 3764.1408 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 14 | HeaderMin_6HeaderMax_14
535 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 4181.2627 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
536 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 4546.0383 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
537 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 4943.7321 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
538 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 4916.0029 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
539 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 5215.731 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
540 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 5615.4961 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 18 | HeaderMin_6HeaderMax_18
541 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 5937.2753 | 4 | 0 | 4 | C | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 18 | HeaderMin_6HeaderMax_18
542 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 4687.6261 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
543 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 5267.7388 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
544 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 5816.9511 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 18 | HeaderMin_8HeaderMax_18
545 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 6274.8868 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 18 | HeaderMin_8HeaderMax_18
546 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 5659.5343 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 18 | HeaderMin_8HeaderMax_18
547 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 6093.4973 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 18 | HeaderMin_8HeaderMax_18
548 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 6500.4683 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
549 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 7029.1185 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
550 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 7387.4035 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 20 | HeaderMin_8HeaderMax_20
551 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 7658.324 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 20 | HeaderMin_8HeaderMax_20
552 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 6537.5317 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
553 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 7661.0951 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 20 | HeaderMin_8HeaderMax_20
554 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 8661.0874 | 4 | 0 | 4 | C | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 20 | HeaderMin_8HeaderMax_20
555 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 7656.5877 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
556 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 8071.9496 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
557 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 8566.398 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
558 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 9162.314 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 24 | HeaderMin_10HeaderMax_24
559 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 6909.9805 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
560 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 7306.7929 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
561 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 8013.4225 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
562 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 8748.7945 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
563 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 9174.6955 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 24 | HeaderMin_10HeaderMax_24
564 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 9689.1937 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 24 | HeaderMin_10HeaderMax_24
565 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 10189.4456 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
566 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 11812.2111 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
567 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 12883.8429 | 4 | 0 | 4 | C | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
568 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 14319.5187 | 4 | 0 | 4 | C | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
569 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 15707.4993 | 4 | 0 | 4 | C | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
570 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 16513.1135 | 4 | 0 | 4 | C | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
571 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 120.9035 | 1 | 1 | 2 | D | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
572 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 134.1949 | 1 | 1 | 2 | D | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
573 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 146.7341 | 1 | 1 | 2 | D | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
574 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 154 | 1 | 1 | 2 | D | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
575 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 79 | 1 | 1 | 2 | D | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 2 | HeaderMin_2.5HeaderMax_2 | Yes
576 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 169.9715 | 1 | 1 | 2 | D | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
577 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 191.939 | 1 | 1 | 2 | D | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
578 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 226.3257 | 1 | 1 | 2 | D | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
579 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 124.0691 | 1 | 1 | 2 | D | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
580 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 190.191 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
581 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 214.0515 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
582 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 249.8523 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
583 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 243.9916 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
584 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 128.156 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
585 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 152.95 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
586 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 168.2305 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
587 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 184.528 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
588 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 191.32 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
589 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 90.3291 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
590 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 95.22 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
591 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 176.1225 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
592 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 200.368 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
593 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 232.5586 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
594 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 232.5586 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
595 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 111.4482 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
596 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 118.6369 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 2.5 | HeaderMin_2.5HeaderMax_2.5
597 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 205.3636 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
598 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 235.6474 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
599 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 257.4 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
600 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 277.4627 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
601 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 300 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
602 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 300 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
603 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 136.1059 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
604 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 162.637 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
605 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 165.3271 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
606 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 271.9533 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
607 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 309.3395 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
608 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 341.2848 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
609 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 380.858 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
610 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 405.1149 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
611 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 406.8778 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
612 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 154.2292 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
613 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 205.8649 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
614 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 227.7916 | 1 | 1 | 2 | D | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
615 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 294.5625 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
616 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 355.8818 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
617 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 415.2757 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
618 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 449.14 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
619 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 222.9265 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
620 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 339.6329 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
621 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 384.0902 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
622 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 424.5536 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
623 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 491.3603 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
624 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 551.7418 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
625 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 573.0512 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 5 | HeaderMin_3HeaderMax_5
626 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 179.981 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 3 | HeaderMin_3HeaderMax_3
627 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 237.9031 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
628 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 284.3868 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
629 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 260.585 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
630 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 273.2839 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
631 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 330.9972 | 1 | 1 | 2 | D | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 4 | HeaderMin_3HeaderMax_4
632 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 524.7552 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
633 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 534.9404 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
634 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 573.9449 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
635 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 599.7227 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
636 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 512.3923 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
637 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 573.8168 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
638 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 630.1667 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
639 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 681.695 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 6 | HeaderMin_4HeaderMax_6
640 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 242.0702 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
641 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 291.6367 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
642 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 290.4936 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
643 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 350.6693 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
644 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 375.4803 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
645 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 402.5638 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
646 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 427.3855 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
647 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 430.0891 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
648 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 453.84 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
649 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 360.7205 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
650 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 391.3696 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 4 | HeaderMin_4HeaderMax_4
651 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 444.5377 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
652 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 455.5928 | 1 | 1 | 2 | D | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 5 | HeaderMin_4HeaderMax_5
653 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 548.8465 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
654 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 628.8755 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
655 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 683.4996 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
656 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 734.2064 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
657 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 789.7994 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
658 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 360.84 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 4 | HeaderMin_5HeaderMax_4 | Yes
659 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 427.4383 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5 | Yes | Yes
660 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 913.8143 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
661 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 969.4037 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
662 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 1015.343 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
663 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 1051.8577 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
664 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 1127.0937 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
665 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 456.5775 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
666 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 508.0798 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
667 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 534.9443 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
668 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 568.82 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
669 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 885.0742 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
670 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 912.6252 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
671 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 955.0129 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
672 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 1024.8269 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
673 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 1116.5838 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 8 | HeaderMin_5HeaderMax_8
674 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 466.2681 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
675 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 509.7501 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
676 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 543.4703 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
677 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 607.7455 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
678 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 667.9 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
679 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 732.8 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
680 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 774.6 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
681 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 813.5 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
682 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 616.3385 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
683 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 707.5905 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
684 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 786.8099 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
685 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 825.5 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
686 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 756.8 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
687 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 830.5 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
688 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 873.3 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
689 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 639.1572 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 5 | HeaderMin_5HeaderMax_5
690 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 794.9133 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
691 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 882.342 | 1 | 1 | 2 | D | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 6 | HeaderMin_5HeaderMax_6
692 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 935.9263 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
693 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 1136.2741 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
694 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 1332.9681 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
695 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 1528.3535 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
696 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 626.346 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 5 | HeaderMin_6HeaderMax_5 | Yes
697 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 764.9699 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
698 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 682.0481 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
699 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 802.7921 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
700 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 932.9167 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
701 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 1000.0001 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
702 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 753.2463 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
703 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 820.4429 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
704 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 953.3171 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
705 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 1029.7585 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
706 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 1330.3437 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
707 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 1378.5213 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
708 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 1467.9509 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
709 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 844.864 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
710 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 982.3526 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
711 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 1104.8611 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
712 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 1214.4257 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
713 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 1383.6857 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
714 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 1551.2098 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
715 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 1664.6746 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 10 | HeaderMin_6HeaderMax_10
716 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 840.7876 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
717 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 995.4751 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
718 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 1093.6698 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
719 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 1144.8546 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
720 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 1204.5001 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
721 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 1252.5 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
722 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 648.3835 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 5 | HeaderMin_6HeaderMax_5 | Yes
723 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 820.3589 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
724 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 941.0352 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 6 | HeaderMin_6HeaderMax_6
725 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 1045.3157 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
726 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 1136.5096 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
727 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 1235.933 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
728 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 1229.0007 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
729 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 1303.9328 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
730 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 1403.874 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
731 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 1484.3188 | 1 | 1 | 2 | D | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 8 | HeaderMin_6HeaderMax_8
732 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 1171.9065 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
733 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 1316.9347 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
734 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 1454.2378 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
735 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 1568.7217 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
736 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 1414.8836 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
737 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 1523.3743 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 8 | HeaderMin_8HeaderMax_8
738 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 1625.1171 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
739 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 1757.2796 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
740 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 1846.8509 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
741 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 1914.581 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
742 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 1634.3829 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
743 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 1915.2738 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
744 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 2165.2718 | 1 | 1 | 2 | D | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 10 | HeaderMin_8HeaderMax_10
745 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 1914.1469 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
746 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 2017.9874 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
747 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 2141.5995 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
748 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 2290.5785 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
749 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 1727.4951 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
750 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 1826.6982 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
751 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 2003.3556 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
752 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 2187.1986 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
753 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 2293.6739 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
754 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 2422.2984 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 10 | HeaderMin_10HeaderMax_10
755 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 2547.3614 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 12 | HeaderMin_10HeaderMax_12
756 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 2953.0528 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 12 | HeaderMin_10HeaderMax_12
757 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 3220.9607 | 1 | 1 | 2 | D | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 12 | HeaderMin_10HeaderMax_12
758 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 3579.8797 | 1 | 1 | 2 | D | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 14 | HeaderMin_12HeaderMax_14
759 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 3926.8748 | 1 | 1 | 2 | D | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 14 | HeaderMin_12HeaderMax_14
760 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 4128.2784 | 1 | 1 | 2 | D | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 14 | HeaderMin_12HeaderMax_14
761 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 241.807 | 2 | 1 | 3 | E | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
762 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 268.3898 | 2 | 1 | 3 | E | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
763 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 293.4682 | 2 | 1 | 3 | E | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
764 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 308 | 2 | 1 | 3 | E | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
765 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 158 | 2 | 1 | 3 | E | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
766 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 339.9431 | 2 | 1 | 3 | E | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
767 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 383.8779 | 2 | 1 | 3 | E | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
768 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 452.6514 | 2 | 1 | 3 | E | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
769 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 248.1382 | 2 | 1 | 3 | E | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
770 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 380.3819 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
771 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 428.1031 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
772 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 499.7046 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
773 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 487.9832 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
774 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 256.3121 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
775 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 305.9 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
776 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 336.461 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
777 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 369.056 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
778 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 382.64 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
779 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 180.6582 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
780 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 190.44 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
781 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 352.2451 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
782 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 400.7361 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
783 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 465.1173 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
784 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 465.1173 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
785 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 222.8964 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
786 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 237.2737 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
787 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 410.7272 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
788 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 471.2947 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
789 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 514.8 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
790 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 554.9253 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
791 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 600 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
792 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 600 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
793 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 272.2118 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
794 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 325.274 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
795 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 330.6542 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
796 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 543.9066 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
797 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 618.679 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
798 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 682.5695 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
799 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 761.716 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
800 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 810.2297 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
801 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 813.7556 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
802 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 308.4583 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
803 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 411.7298 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
804 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 455.5833 | 2 | 1 | 3 | E | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
805 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 589.1251 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
806 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 711.7636 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
807 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 830.5515 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
808 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 898.2801 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
809 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 445.8531 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
810 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 679.2659 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
811 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 768.1804 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
812 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 849.1072 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
813 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 982.7205 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
814 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 1103.4836 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
815 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 1146.1024 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
816 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 359.9621 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 4 | HeaderMin_3HeaderMax_4
817 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 475.8063 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
818 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 568.7735 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
819 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 521.17 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
820 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 546.5679 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
821 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 661.9944 | 2 | 1 | 3 | E | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
822 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 1049.5105 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
823 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 1069.8809 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
824 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 1147.8898 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
825 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 1199.4453 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
826 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 1024.7846 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
827 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 1147.6336 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
828 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 1260.3334 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
829 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 1363.39 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 8 | HeaderMin_4HeaderMax_8
830 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 484.1403 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
831 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 583.2733 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
832 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 580.9873 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
833 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 701.3387 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
834 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 750.9605 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
835 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 805.1276 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
836 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 854.771 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
837 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 860.1783 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
838 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 907.68 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
839 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 721.4409 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
840 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 782.7393 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
841 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 889.0754 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
842 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 911.1855 | 2 | 1 | 3 | E | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
843 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 1097.6931 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
844 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 1257.751 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
845 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 1366.9992 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
846 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 1468.4128 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
847 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 1579.5988 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
848 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 721.68 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 6 | HeaderMin_5HeaderMax_6
849 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 854.8766 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6 | Yes | Yes
850 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 1827.6287 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
851 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 1938.8074 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
852 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 2030.6859 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
853 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 2103.7154 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
854 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 2254.1875 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
855 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 913.1549 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
856 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 1016.1596 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
857 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 1069.8887 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
858 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 1137.64 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
859 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 1770.1484 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
860 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 1825.2504 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
861 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 1910.0257 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
862 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 2049.6538 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
863 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 2233.1676 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
864 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 932.5363 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
865 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 1019.5003 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
866 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 1086.9406 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
867 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 1215.4911 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
868 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 1335.8 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
869 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 1465.6 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
870 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 1549.2 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
871 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 1627 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
872 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 1232.6769 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
873 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 1415.1811 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
874 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 1573.6198 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
875 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 1651 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
876 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 1513.6 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
877 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 1661 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
878 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 1746.6 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
879 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 1278.3144 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
880 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 1589.8266 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
881 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 1764.6841 | 2 | 1 | 3 | E | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
882 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 1871.8526 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
883 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 2272.5482 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
884 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 2665.9362 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
885 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 3056.707 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
886 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 1252.6919 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
887 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 1529.9399 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
888 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 1364.0961 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
889 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 1605.5841 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
890 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 1865.8335 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
891 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 2000.0002 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
892 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 1506.4926 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
893 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 1640.8858 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
894 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 1906.6342 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
895 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 2059.5169 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
896 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 2660.6874 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
897 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 2757.0426 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
898 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 2935.9018 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
899 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 1689.7279 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
900 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 1964.7052 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
901 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 2209.7222 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
902 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 2428.8514 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
903 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 2767.3715 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
904 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 3102.4196 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
905 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 3329.3491 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 12 | HeaderMin_6HeaderMax_12
906 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 1681.5751 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
907 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 1990.9502 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
908 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 2187.3397 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
909 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 2289.7092 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
910 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 2409.0002 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
911 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 2505 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
912 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 1296.767 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
913 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 1640.7178 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
914 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 1882.0704 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
915 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 2090.6314 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
916 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 2273.0192 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
917 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 2471.866 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
918 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 2458.0014 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
919 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 2607.8655 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
920 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 2807.748 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
921 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 2968.6376 | 2 | 1 | 3 | E | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
922 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 2343.8131 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 10 | HeaderMin_8HeaderMax_10
923 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 2633.8694 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
924 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 2908.4756 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
925 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 3137.4434 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
926 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 2829.7672 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
927 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 3046.7486 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
928 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 3250.2342 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
929 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 3514.5593 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
930 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 3693.7017 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
931 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 3829.162 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
932 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 3268.7658 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
933 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 3830.5476 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
934 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 4330.5437 | 2 | 1 | 3 | E | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
935 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 3828.2938 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
936 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 4035.9748 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
937 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 4283.199 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
938 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 4581.157 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
939 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 3454.9903 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 12 | HeaderMin_10HeaderMax_12
940 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 3653.3965 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
941 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 4006.7112 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
942 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 4374.3972 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
943 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 4587.3477 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
944 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 4844.5968 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
945 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 5094.7228 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 16 | HeaderMin_10HeaderMax_16
946 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 5906.1056 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
947 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 6441.9215 | 2 | 1 | 3 | E | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
948 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 7159.7593 | 2 | 1 | 3 | E | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
949 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 7853.7497 | 2 | 1 | 3 | E | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
950 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 8256.5567 | 2 | 1 | 3 | E | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
951 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 362.7105 | 3 | 1 | 4 | F | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
952 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 402.5848 | 3 | 1 | 4 | F | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
953 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 440.2024 | 3 | 1 | 4 | F | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
954 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 462 | 3 | 1 | 4 | F | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
955 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 237 | 3 | 1 | 4 | F | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
956 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 509.9146 | 3 | 1 | 4 | F | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
957 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 575.8169 | 3 | 1 | 4 | F | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
958 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 678.977 | 3 | 1 | 4 | F | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
959 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 372.2073 | 3 | 1 | 4 | F | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
960 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 570.5729 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
961 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 642.1546 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
962 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 749.5569 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
963 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 731.9747 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
964 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 384.4681 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
965 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 458.85 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
966 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 504.6915 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
967 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 553.584 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
968 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 573.96 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
969 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 270.9873 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
970 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 285.66 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
971 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 528.3676 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
972 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 601.1041 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
973 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 697.6759 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
974 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 697.6759 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
975 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 334.3446 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
976 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 355.9106 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
977 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 616.0908 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
978 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 706.9421 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
979 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 772.2001 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
980 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 832.388 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
981 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 900 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
982 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 900 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
983 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 408.3177 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
984 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 487.911 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
985 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 495.9813 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
986 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 815.8599 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
987 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 928.0185 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
988 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 1023.8543 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
989 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 1142.5741 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
990 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 1215.3446 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
991 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 1220.6335 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 8 | HeaderMin_2.5HeaderMax_8
992 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 462.6875 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
993 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 617.5946 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
994 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 683.3749 | 3 | 1 | 4 | F | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
995 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 883.6876 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
996 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 1067.6453 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
997 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 1245.8272 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
998 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 1347.4201 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
999 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 668.7796 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1000 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 1018.8988 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
1001 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 1152.2706 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
1002 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 1273.6608 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
1003 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 1474.0808 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
1004 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 1655.2254 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
1005 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 1719.1537 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 10 | HeaderMin_3HeaderMax_10
1006 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 539.9431 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 5 | HeaderMin_3HeaderMax_5
1007 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 713.7094 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1008 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 853.1603 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1009 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 781.755 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1010 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 819.8518 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1011 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 992.9917 | 3 | 1 | 4 | F | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 8 | HeaderMin_3HeaderMax_8
1012 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 1574.2657 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1013 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 1604.8213 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
1014 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 1721.8346 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
1015 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 1799.168 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
1016 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 1537.1769 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1017 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 1721.4503 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
1018 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 1890.5 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 10 | HeaderMin_4HeaderMax_10
1019 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 2045.085 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 10 | HeaderMin_4HeaderMax_10
1020 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 726.2105 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1021 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 874.91 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1022 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 871.4809 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1023 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 1052.008 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
1024 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 1126.4408 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
1025 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 1207.6913 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1026 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 1282.1565 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1027 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 1290.2674 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1028 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 1361.52 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1029 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 1082.1614 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
1030 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 1174.1089 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 8 | HeaderMin_4HeaderMax_8
1031 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 1333.6131 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1032 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 1366.7783 | 3 | 1 | 4 | F | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1033 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 1646.5396 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1034 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 1886.6265 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1035 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 2050.4988 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1036 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 2202.6191 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1037 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 2369.3983 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1038 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 1082.52 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 8 | HeaderMin_5HeaderMax_8
1039 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 1282.3149 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8 | Yes | Yes
1040 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 2741.443 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
1041 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 2908.2111 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1042 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 3046.0289 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1043 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 3155.5731 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1044 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 3381.2812 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1045 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 1369.7324 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1046 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 1524.2394 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1047 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 1604.833 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1048 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 1706.46 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1049 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 2655.2225 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
1050 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 2737.8756 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
1051 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 2865.0386 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1052 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 3074.4806 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1053 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 3349.7514 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 12 | HeaderMin_5HeaderMax_12
1054 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 1398.8044 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1055 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 1529.2504 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1056 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 1630.411 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1057 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 1823.2366 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1058 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 2003.7 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1059 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 2198.4 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1060 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 2323.8 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1061 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 2440.5 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1062 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 1849.0154 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1063 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 2122.7716 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1064 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 2360.4297 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1065 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 2476.5 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1066 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 2270.4 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1067 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 2491.5 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1068 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 2619.9 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
1069 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 1917.4715 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 10 | HeaderMin_5HeaderMax_10
1070 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 2384.7399 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1071 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 2647.0261 | 3 | 1 | 4 | F | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 12 | HeaderMin_5HeaderMax_12
1072 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 2807.7789 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
1073 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 3408.8222 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1074 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 3998.9043 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1075 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 4585.0605 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
1076 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 1879.0379 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 10 | HeaderMin_6HeaderMax_10
1077 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 2294.9098 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1078 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 2046.1442 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1079 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 2408.3762 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1080 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 2798.7502 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
1081 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 3000.0002 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1082 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 2259.739 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1083 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 2461.3287 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1084 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 2859.9513 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1085 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 3089.2754 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1086 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 3991.0312 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1087 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 4135.5639 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1088 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 4403.8528 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
1089 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 2534.5919 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
1090 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 2947.0578 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1091 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 3314.5834 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1092 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 3643.277 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1093 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 4151.0572 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1094 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 4653.6293 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
1095 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 4994.0237 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 16 | HeaderMin_6HeaderMax_16
1096 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 2522.3627 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
1097 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 2986.4252 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1098 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 3281.0095 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1099 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 3434.5638 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1100 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 3613.5003 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1101 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 3757.5 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1102 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 1945.1505 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 10 | HeaderMin_6HeaderMax_10
1103 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 2461.0767 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1104 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 2823.1056 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 12 | HeaderMin_6HeaderMax_12
1105 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 3135.947 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1106 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 3409.5287 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1107 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 3707.799 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1108 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 3687.0022 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1109 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 3911.7983 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1110 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 4211.6221 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 14 | HeaderMin_6HeaderMax_14
1111 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 4452.9564 | 3 | 1 | 4 | F | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 16 | HeaderMin_6HeaderMax_16
1112 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 3515.7196 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1113 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 3950.8041 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 14 | HeaderMin_8HeaderMax_14
1114 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 4362.7133 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
1115 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 4706.1651 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
1116 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 4244.6507 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 14 | HeaderMin_8HeaderMax_14
1117 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 4570.123 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 16 | HeaderMin_8HeaderMax_16
1118 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 4875.3512 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
1119 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 5271.8389 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
1120 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 5540.5526 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
1121 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 5743.743 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
1122 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 4903.1487 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
1123 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 5745.8213 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
1124 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 6495.8155 | 3 | 1 | 4 | F | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 18 | HeaderMin_8HeaderMax_18
1125 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 5742.4408 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1126 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 6053.9622 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1127 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 6424.7985 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1128 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 6871.7355 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1129 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 5182.4854 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1130 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 5480.0947 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1131 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 6010.0669 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1132 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 6561.5959 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1133 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 6881.0216 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 18 | HeaderMin_10HeaderMax_18
1134 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 7266.8952 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 20 | HeaderMin_10HeaderMax_20
1135 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 7642.0842 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 20 | HeaderMin_10HeaderMax_20
1136 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 8859.1584 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
1137 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 9662.8822 | 3 | 1 | 4 | F | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 24 | HeaderMin_10HeaderMax_24
1138 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 10739.639 | 3 | 1 | 4 | F | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
1139 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 11780.6245 | 3 | 1 | 4 | F | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
1140 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 12384.8351 | 3 | 1 | 4 | F | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 24 | HeaderMin_12HeaderMax_24
1141 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 483.6139 | 4 | 1 | 5 | G | VLS_Inline | 1.25 | 1.25 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1142 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 536.7797 | 4 | 1 | 5 | G | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1143 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 586.9365 | 4 | 1 | 5 | G | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1144 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 616 | 4 | 1 | 5 | G | VLS_Inline | 1.25 | 1.25 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1145 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 316 | 4 | 1 | 5 | G | VLS_Inline | 1.25 | 1.25 | 2 | 2 | BranchMin_2BranchMax_2 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
1146 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 679.8862 | 4 | 1 | 5 | G | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1147 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 767.7559 | 4 | 1 | 5 | G | VLS_Inline | 1.5 | 1.5 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1148 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 905.3027 | 4 | 1 | 5 | G | VLS_Inline | 1.5 | 1.5 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1149 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 496.2764 | 4 | 1 | 5 | G | VLS_Inline | 1.5 | 1.5 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1150 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 760.7639 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1151 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 856.2061 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1152 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 999.4092 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1153 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 975.9663 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1154 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 512.6241 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1155 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 611.8001 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1156 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 672.9221 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1157 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 738.1121 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1158 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 765.2801 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1159 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 361.3164 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
1160 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 380.88 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 3 | HeaderMin_2.5HeaderMax_3
1161 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 704.4902 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1162 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 801.4722 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1163 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 930.2345 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1164 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 930.2345 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1165 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 445.7928 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1166 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 474.5474 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 2.5 | BranchMin_2BranchMax_2.5 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1167 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 821.4543 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1168 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 942.5895 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1169 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 1029.6001 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1170 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 1109.8506 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1171 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 1200 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1172 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 1200 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1173 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 544.4236 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1174 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 650.548 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1175 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 661.3083 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1176 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 1087.8131 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1177 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 1237.358 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1178 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 1365.139 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
1179 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 1523.4321 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
1180 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 1620.4594 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
1181 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 1627.5113 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 5 | BranchMin_2BranchMax_5 | 2.5 | 6 | HeaderMin_2.5HeaderMax_6
1182 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 616.9167 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 4 | HeaderMin_2.5HeaderMax_4
1183 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 823.4595 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 3 | BranchMin_2BranchMax_3 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1184 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 911.1665 | 4 | 1 | 5 | G | VLS_Inline | 2 | 2 | 2 | 4 | BranchMin_2BranchMax_4 | 2.5 | 5 | HeaderMin_2.5HeaderMax_5
1185 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 1178.2501 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1186 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 1423.5271 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1187 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 1661.103 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
1188 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 1796.5602 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
1189 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 891.7062 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1190 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 1358.5317 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1191 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 1536.3608 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1192 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 1698.2144 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 6 | HeaderMin_3HeaderMax_6
1193 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 1965.4411 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
1194 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 2206.9672 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
1195 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 2292.2049 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 5 | BranchMin_2.5BranchMax_5 | 3 | 8 | HeaderMin_3HeaderMax_8
1196 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 719.9241 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 3 | BranchMin_2.5BranchMax_3 | 3 | 4 | HeaderMin_3HeaderMax_4
1197 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 951.6126 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1198 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 1137.547 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1199 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 1042.34 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1200 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 1093.1357 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 5 | HeaderMin_3HeaderMax_5
1201 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 1323.9889 | 4 | 1 | 5 | G | VLS_Inline | 2.5 | 2.5 | 2.5 | 4 | BranchMin_2.5BranchMax_4 | 3 | 6 | HeaderMin_3HeaderMax_6
1202 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 2099.021 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1203 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 2139.7617 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1204 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 2295.7795 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1205 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 2398.8907 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1206 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 2049.5692 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1207 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 2295.2671 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1208 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 2520.6667 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 8 | HeaderMin_4HeaderMax_8
1209 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 2726.78 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 6 | BranchMin_3BranchMax_6 | 4 | 8 | HeaderMin_4HeaderMax_8
1210 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 968.2806 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
1211 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 1166.5466 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
1212 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 1161.9746 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 5 | HeaderMin_4HeaderMax_5
1213 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 1402.6774 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1214 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 1501.921 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1215 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 1610.2551 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1216 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 1709.542 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1217 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 1720.3565 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1218 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 1815.36 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1219 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 1442.8819 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1220 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 1565.4785 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 4 | BranchMin_3BranchMax_4 | 4 | 6 | HeaderMin_4HeaderMax_6
1221 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 1778.1508 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1222 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 1822.371 | 4 | 1 | 5 | G | VLS_Inline | 3 | 3 | 3 | 5 | BranchMin_3BranchMax_5 | 4 | 6 | HeaderMin_4HeaderMax_6
1223 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 2195.3862 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1224 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 2515.502 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1225 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 2733.9985 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1226 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 2936.8255 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1227 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 3159.1977 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1228 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 1443.36 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 4 | BranchMin_4BranchMax_4 | 5 | 6 | HeaderMin_5HeaderMax_6
1229 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 427.4383 | 427.4383 | 1709.7532 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 3 | HeaderMin_5HeaderMax_3 | Yes | Yes
1230 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 3655.2573 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1231 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 3877.6149 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1232 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 4061.3719 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1233 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 4207.4307 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1234 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 4508.3749 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1235 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 1826.3098 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
1236 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 2032.3192 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1237 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 2139.7774 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1238 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 2275.28 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1239 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 3540.2967 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1240 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 3650.5009 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1241 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 3820.0514 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1242 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 4099.3075 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1243 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 4466.3352 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 8 | BranchMin_4BranchMax_8 | 5 | 10 | HeaderMin_5HeaderMax_10
1244 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 1865.0725 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 6 | HeaderMin_5HeaderMax_6
1245 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 2039.0006 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1246 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 2173.8813 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1247 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 2430.9822 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1248 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 2671.6 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1249 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 2931.2 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1250 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 3098.4 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1251 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 3254 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1252 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 2465.3539 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1253 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 2830.3621 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1254 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 3147.2397 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1255 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 3302 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1256 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 3027.2 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1257 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 3322 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1258 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 3493.2 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1259 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 2556.6287 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 5 | BranchMin_4BranchMax_5 | 5 | 8 | HeaderMin_5HeaderMax_8
1260 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 3179.6532 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 8 | HeaderMin_5HeaderMax_8
1261 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 3529.3682 | 4 | 1 | 5 | G | VLS_Inline | 4 | 4 | 4 | 6 | BranchMin_4BranchMax_6 | 5 | 10 | HeaderMin_5HeaderMax_10
1262 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 3743.7052 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1263 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 4545.0963 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1264 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 5331.8724 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1265 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 6113.414 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1266 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 2505.3838 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
1267 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 3059.8797 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
1268 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 2728.1922 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
1269 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 3211.1683 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1270 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 3731.667 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1271 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 4000.0003 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1272 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 3012.9853 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 8 | HeaderMin_6HeaderMax_8
1273 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 3281.7717 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1274 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 3813.2684 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1275 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 4119.0339 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1276 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 5321.3749 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1277 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 5514.0852 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1278 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 5871.8037 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1279 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 3379.4558 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1280 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 3929.4104 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1281 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 4419.4445 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1282 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 4857.7027 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1283 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 5534.743 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1284 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 6204.8391 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1285 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 6658.6983 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 10 | BranchMin_5BranchMax_10 | 6 | 12 | HeaderMin_6HeaderMax_12
1286 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 3363.1503 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1287 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 3981.9003 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1288 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 4374.6794 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1289 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 4579.4184 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1290 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 4818.0004 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1291 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 5010 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1292 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 2593.534 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 5 | BranchMin_5BranchMax_5 | 6 | 8 | HeaderMin_6HeaderMax_8
1293 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 3281.4355 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1294 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 3764.1408 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 6 | BranchMin_5BranchMax_6 | 6 | 10 | HeaderMin_6HeaderMax_10
1295 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 4181.2627 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1296 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 4546.0383 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1297 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 4943.7321 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1298 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 4916.0029 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 10 | HeaderMin_6HeaderMax_10
1299 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 5215.731 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1300 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 5615.4961 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1301 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 5937.2753 | 4 | 1 | 5 | G | VLS_Inline | 5 | 5 | 5 | 8 | BranchMin_5BranchMax_8 | 6 | 12 | HeaderMin_6HeaderMax_12
1302 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 4687.6261 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 10 | HeaderMin_8HeaderMax_10
1303 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 5267.7388 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1304 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 5816.9511 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1305 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 6274.8868 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1306 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 5659.5343 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1307 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 6093.4973 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 8 | BranchMin_6BranchMax_8 | 8 | 12 | HeaderMin_8HeaderMax_12
1308 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 6500.4683 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
1309 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 7029.1185 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
1310 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 7387.4035 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
1311 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 7658.324 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
1312 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 6537.5317 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 12 | HeaderMin_8HeaderMax_12
1313 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 7661.0951 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 14 | HeaderMin_8HeaderMax_14
1314 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 8661.0874 | 4 | 1 | 5 | G | VLS_Inline | 6 | 6 | 6 | 10 | BranchMin_6BranchMax_10 | 8 | 16 | HeaderMin_8HeaderMax_16
1315 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 7656.5877 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
1316 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 8071.9496 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
1317 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 8566.398 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1318 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 9162.314 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1319 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 6909.9805 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 12 | HeaderMin_10HeaderMax_12
1320 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 7306.7929 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
1321 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 8013.4225 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 14 | HeaderMin_10HeaderMax_14
1322 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 8748.7945 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1323 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 9174.6955 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1324 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 9689.1937 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 10 | BranchMin_8BranchMax_10 | 10 | 16 | HeaderMin_10HeaderMax_16
1325 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 10189.4456 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 16 | HeaderMin_10HeaderMax_16
1326 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 11812.2111 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
1327 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 12883.8429 | 4 | 1 | 5 | G | VLS_Inline | 8 | 8 | 8 | 12 | BranchMin_8BranchMax_12 | 10 | 18 | HeaderMin_10HeaderMax_18
1328 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 14319.5187 | 4 | 1 | 5 | G | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
1329 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 15707.4993 | 4 | 1 | 5 | G | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20
1330 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 16513.1135 | 4 | 1 | 5 | G | VLS_Inline | 10 | 10 | 10 | 14 | BranchMin_10BranchMax_14 | 12 | 20 | HeaderMin_12HeaderMax_20

## Sheet1
Branch Range | Branch Range, List | Header Range | Header Range, List
BranchMin_2BranchMax_2.5 | 2,2.5 | HeaderMin_2.5HeaderMax_4 | 2.5,3,4
BranchMin_2BranchMax_3 | 2,2.5,3 | HeaderMin_2.5HeaderMax_3 | 2.5,3
BranchMin_2BranchMax_2 | 2 | HeaderMin_2.5HeaderMax_5 | 2.5,3,4,5
BranchMin_2BranchMax_4 | 2,2.5,3,4 | HeaderMin_2.5HeaderMax_6 | 2.5,3,4,5,6
BranchMin_2BranchMax_5 | 2,2.5,3,4,5 | HeaderMin_3HeaderMax_5 | 3,4,5
BranchMin_2.5BranchMax_4 | 2.5,3,4 | HeaderMin_3HeaderMax_6 | 3,4,5,6
BranchMin_2.5BranchMax_5 | 2.5,3,4,5 | HeaderMin_3HeaderMax_8 | 3,4,5,6,8
BranchMin_2.5BranchMax_3 | 2.5,3 | HeaderMin_3HeaderMax_4 | 3,4
BranchMin_3BranchMax_5 | 3,4,5 | HeaderMin_4HeaderMax_8 | 4,5,6,8
BranchMin_3BranchMax_6 | 3,4,5,6 | HeaderMin_4HeaderMax_5 | 4,5
BranchMin_3BranchMax_4 | 3,4 | HeaderMin_4HeaderMax_6 | 4,5,6
BranchMin_4BranchMax_5 | 4,5 | HeaderMin_5HeaderMax_8 | 5,6,8
BranchMin_4BranchMax_6 | 4,5,6 | HeaderMin_5HeaderMax_6 | 5,6
BranchMin_4BranchMax_4 | 4 | HeaderMin_5HeaderMax_3 | X
BranchMin_4BranchMax_2.5 | X | HeaderMin_5HeaderMax_10 | 5,6,8,10
BranchMin_4BranchMax_8 | 4,5,6,8 | HeaderMin_6HeaderMax_10 | 6,8,10
BranchMin_5BranchMax_6 | 5,6 | HeaderMin_6HeaderMax_12 | 6,8,10,12
BranchMin_5BranchMax_8 | 5,6,8 | HeaderMin_6HeaderMax_8 | 6,8
BranchMin_5BranchMax_5 | 5 | HeaderMin_8HeaderMax_10 | 8,10
BranchMin_5BranchMax_10 | 5,6,8,10 | HeaderMin_8HeaderMax_12 | 8,10,12
BranchMin_6BranchMax_8 | 6,8 | HeaderMin_8HeaderMax_14 | 8,10,12,14
BranchMin_6BranchMax_10 | 6,8,10 | HeaderMin_8HeaderMax_16 | 8,10,12,14,16
BranchMin_8BranchMax_10 | 8,10 | HeaderMin_10HeaderMax_14 | 10,12,14
BranchMin_8BranchMax_12 | 8,10,12 | HeaderMin_10HeaderMax_16 | 10,12,14,16
BranchMin_10BranchMax_14 | 10,12,14 | HeaderMin_10HeaderMax_12 | 10,12
|  | HeaderMin_10HeaderMax_18 | 10,12,14,16,18
|  | HeaderMin_12HeaderMax_20 | 12,14,16,18,20
|  | HeaderMin_2.5HeaderMax_8 | 2.5,4,6,8
|  | HeaderMin_3HeaderMax_10 | 3,4,5,6,8,10
|  | HeaderMin_4HeaderMax_10 | 4,5,6,8,10
|  | HeaderMin_5HeaderMax_4 | X
|  | HeaderMin_5HeaderMax_12 | 5,6,8,10,12
|  | HeaderMin_6HeaderMax_14 | 6,8,10,12,14
|  | HeaderMin_6HeaderMax_16 | 6,8,10,12,14,16
|  | HeaderMin_8HeaderMax_18 | 8,10,12,14,16,18
|  | HeaderMin_10HeaderMax_20 | 10,12,14,16,18,20
|  | HeaderMin_10HeaderMax_24 | 10,12,14,16,18,20,24
|  | HeaderMin_12HeaderMax_24 | 12,14,16,18,20,24
|  | HeaderMin_2.5HeaderMax_10 | 2.5,4,6,8,10
|  | HeaderMin_4HeaderMax_12 | 4,5,6,8,10,12
|  | HeaderMin_5HeaderMax_5 | 5
|  | HeaderMin_5HeaderMax_14 | 5,6,8,10,12,14
|  | HeaderMin_5HeaderMax_16 | 5,6,8,10,12,14,16
|  | HeaderMin_6HeaderMax_18 | 6,8,10,12,14,16,18
|  | HeaderMin_8HeaderMax_20 | 8,10,12,14,16,18,20
|  | HeaderMin_2.5HeaderMax_2.5 | 2.5
|  | HeaderMin_2.5HeaderMax_2 | X
|  | HeaderMin_3HeaderMax_3 | 3
|  | HeaderMin_4HeaderMax_4 | 4
|  | HeaderMin_5HeaderMax_2.5 | X
|  | HeaderMin_6HeaderMax_6 | 6
HeaderMin_6HeaderMax_5
|  | HeaderMin_8HeaderMax_8 | 8
|  | HeaderMin_10HeaderMax_10 | 10
|  | HeaderMin_12HeaderMax_14 | 12,14

## Branch to Header min
Branch Minimum
2 | 2.5
2.5 | 3
3 | 4
4 | 5
5 | 6
6 | 8
8 | 10
10 | 12

## Max flow to diameter, Rev1
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.) | Flow (gpm) | Pipe Diameter (in.)
120.9035 | 2.5 | 241.807 | 4 | 20 | 2
134.1949 | 3 | 268.3898 | 4 | 25 | 2
146.7341 |  | 293.4682 |  | 30 | 2
154 |  | 308 |  | 35 | 2
79 |  | 158 |  | 40 | 2
169.9715 |  | 339.9431 |  | 45 | 2
191.939 |  | 383.8779 |  | 50 | 2
226.3257 |  | 452.6514 |  | 55 | 2
124.0691 |  | 248.1382 |  | 60 | 2
190.191 |  | 380.3819 |  | 65 | 2
214.0515 |  | 428.1031 |  | 70 | 2
249.8523 |  | 499.7046 |  | 75 | 2
243.9916 |  | 487.9832 |  | 80 | 2
128.156 |  | 256.3121 |  | 85 | 2.5
152.95 |  | 305.9 |  | 90 | 2.5
168.2305 |  | 336.461 |  | 95 | 2.5
184.528 |  | 369.056 |  | 100 | 2.5
191.32 |  | 382.64 |  | 105 | 2.5
90.3291 |  | 180.6582 |  | 110 | 2.5
95.22 |  | 190.44 |  | 115 | 2.5
176.1225 |  | 352.2451 |  | 120 | 2.5
200.368 |  | 400.7361 |  | 125 | 3
232.5586 |  | 465.1173 |  | 130 | 3
232.5586 |  | 465.1173 |  | 135 | 3
111.4482 |  | 222.8964 |  | 140 | 3
118.6369 |  | 237.2737 |  | 145 | 3
205.3636 |  | 410.7272 |  | 150 | 3
235.6474 |  | 471.2947 |  | 155 | 3
257.4 |  | 514.8 |  | 160 | 3
277.4627 |  | 554.9253 |  | 165 | 3
300 |  | 600 |  | 170 | 3
300 |  | 600 |  | 175 | 3
136.1059 |  | 272.2118 |  | 180 | 3
162.637 |  | 325.274 |  | 185 | 3
165.3271 |  | 330.6542 |  | 190 | 3
271.9533 |  | 543.9066 |  | 195 | 3
309.3395 |  | 618.679 |  | 200 | 3
341.2848 |  | 682.5695 |  | 205 | 3
380.858 |  | 761.716 |  | 210 | 3
405.1149 |  | 810.2297 |  | 215 | 4
406.8778 |  | 813.7556 |  | 220 | 4
154.2292 |  | 308.4583 |  | 225 | 4
205.8649 |  | 411.7298 |  | 230 | 4
227.7916 |  | 455.5833 |  | 235 | 4
294.5625 |  | 589.1251 |  | 240 | 4
355.8818 |  | 711.7636 |  | 245 | 4
415.2757 |  | 830.5515 |  | 250 | 4
449.14 |  | 898.2801 |  | 255 | 4
222.9265 |  | 445.8531 |  | 260 | 4
339.6329 |  | 679.2659 |  | 265 | 4
384.0902 |  | 768.1804 |  | 270 | 4
424.5536 |  | 849.1072 |  | 275 | 4
491.3603 |  | 982.7205 |  | 280 | 4
551.7418 |  | 1103.4836 |  | 285 | 4
573.0512 |  | 1146.1024 |  | 290 | 4
179.981 |  | 359.9621 |  | 295 | 4
237.9031 |  | 475.8063 |  | 300 | 4
284.3868 |  | 568.7735 |  | 305 | 4
260.585 |  | 521.17 |  | 310 | 4
273.2839 |  | 546.5679 |  | 315 | 4
330.9972 |  | 661.9944 |  | 320 | 4
524.7552 |  | 1049.5105 |  | 325 | 4
534.9404 |  | 1069.8809 |  | 330 | 4
573.9449 |  | 1147.8898 |  | 335 | 4
599.7227 |  | 1199.4453 |  | 340 | 4
512.3923 |  | 1024.7846 |  | 345 | 4
573.8168 |  | 1147.6336 |  | 350 | 4
630.1667 |  | 1260.3334 |  | 355 | 4
681.695 |  | 1363.39 |  | 360 | 4
242.0702 |  | 484.1403 |  | 365 | 4
291.6367 |  | 583.2733 |  | 370 | 4
290.4936 |  | 580.9873 |  | 375 | 4
350.6693 |  | 701.3387 |  | 380 | 4
375.4803 |  | 750.9605 |  | 385 | 4
402.5638 |  | 805.1276 |  | 390 | 4
427.3855 |  | 854.771 |  | 395 | 4
430.0891 |  | 860.1783 |  | 400 | 5
453.84 |  | 907.68 |  | 450 | 5
360.7205 |  | 721.4409 |  | 500 | 5
391.3696 |  | 782.7393 |  | 550 | 5
444.5377 |  | 889.0754 |  | 600 | 5
455.5928 |  | 911.1855 |  | 650 | 6
548.8465 |  | 1097.6931 |  | 700 | 6
628.8755 |  | 1257.751 |  | 750 | 6
683.4996 |  | 1366.9992 |  | 800 | 6
734.2064 |  | 1468.4128 |  | 850 | 6
789.7994 |  | 1579.5988 |  | 900 | 6
360.84 |  | 721.68 |  | 950 | 8
427.4383 |  | 854.8766 |  | 1000 | 8
913.8143 |  | 1827.6287 |  | 1050 | 8
969.4037 |  | 1938.8074 |  | 1100 | 8
1015.343 |  | 2030.6859 |  | 1150 | 8
1051.8577 |  | 2103.7154 |  | 1200 | 8
1127.0937 |  | 2254.1875 |  | 1250 | 8
456.5775 |  | 913.1549 |  | 1300 | 8
508.0798 |  | 1016.1596 |  | 1350 | 8
534.9443 |  | 1069.8887 |  | 1400 | 8
568.82 |  | 1137.64 |  | 1450 | 8
885.0742 |  | 1770.1484 |  | 1500 | 8
912.6252 |  | 1825.2504 |  | 1550 | 8
955.0129 |  | 1910.0257 |  | 1600 | 10
1024.8269 |  | 2049.6538 |  | 1650 | 10
1116.5838 |  | 2233.1676 |  | 1700 | 10
466.2681 |  | 932.5363 |  | 1750 | 10
509.7501 |  | 1019.5003 |  | 1800 | 10
543.4703 |  | 1086.9406 |  | 1850 | 10
607.7455 |  | 1215.4911 |  | 1900 | 10
667.9 |  | 1335.8 |  | 1950 | 10
732.8 |  | 1465.6 |  | 2000 | 10
774.6 |  | 1549.2 |  | 2050 | 10
813.5 |  | 1627 |  | 2100 | 10
616.3385 |  | 1232.6769 |  | 2150 | 10
707.5905 |  | 1415.1811 |  | 2200 | 10
786.8099 |  | 1573.6198 |  | 2250 | 10
825.5 |  | 1651 |  | 2300 | 10
756.8 |  | 1513.6 |  | 2350 | 10
830.5 |  | 1661 |  | 2400 | 10
873.3 |  | 1746.6 |  | 2450 | 10
639.1572 |  | 1278.3144 |  | 2500 | 12
794.9133 |  | 1589.8266 |  | 2550 | 12
882.342 |  | 1764.6841 |  | 2600 | 12
935.9263 |  | 1871.8526 |  | 2650 | 12
1136.2741 |  | 2272.5482 |  | 2700 | 12
1332.9681 |  | 2665.9362 |  | 2750 | 12
1528.3535 |  | 3056.707 |  | 2800 | 12
626.346 |  | 1252.6919 |  | 2850 | 12
764.9699 |  | 1529.9399 |  | 2900 | 12
682.0481 |  | 1364.0961 |  | 2950 | 12
802.7921 |  | 1605.5841 |  | 3000 | 12
932.9167 |  | 1865.8335 |  | 3050 | 12
1000.0001 |  | 2000.0002 |  | 3100 | 12
753.2463 |  | 1506.4926 |  | 3150 | 12
820.4429 |  | 1640.8858 |  | 3200 | 12
953.3171 |  | 1906.6342 |  | 3250 | 12
1029.7585 |  | 2059.5169 |  | 3300 | 12
1330.3437 |  | 2660.6874 |  | 3350 | 12
1378.5213 |  | 2757.0426 |  | 3400 | 12
1467.9509 |  | 2935.9018 |  | 3450 | 12
844.864 |  | 1689.7279 |  | 3500 | 12
982.3526 |  | 1964.7052 |  | 3550 | 14
1104.8611 |  | 2209.7222 |  | 3600 | 14
1214.4257 |  | 2428.8514 |  | 3650 | 14
1383.6857 |  | 2767.3715 |  | 3700 | 14
1551.2098 |  | 3102.4196 |  | 3750 | 14
1664.6746 |  | 3329.3491 |  | 3800 | 14
840.7876 |  | 1681.5751 |  | 3850 | 14
995.4751 |  | 1990.9502 |  | 3900 | 14
1093.6698 |  | 2187.3397 |  | 3950 | 14
1144.8546 |  | 2289.7092 |  | 4000 | 14
1204.5001 |  | 2409.0002 |  | 4050 | 14
1252.5 |  | 2505 |  | 4100 | 14
648.3835 |  | 1296.767 |  | 4150 | 14
820.3589 |  | 1640.7178 |  | 4200 | 14
941.0352 |  | 1882.0704 |  | 4250 | 16
1045.3157 |  | 2090.6314 |  | 4300 | 16
1136.5096 |  | 2273.0192 |  | 4350 | 16
1235.933 |  | 2471.866 |  | 4400 | 16
1229.0007 |  | 2458.0014 |  | 4450 | 16
1303.9328 |  | 2607.8655 |  | 4500 | 16
1403.874 |  | 2807.748 |  | 4550 | 16
1484.3188 |  | 2968.6376 |  | 4600 | 16
1171.9065 |  | 2343.8131 |  | 4650 | 16
1316.9347 |  | 2633.8694 |  | 4700 | 16
1454.2378 |  | 2908.4756 |  | 4750 | 16
1568.7217 |  | 3137.4434 |  | 4800 | 16
1414.8836 |  | 2829.7672 |  | 4850 | 16
1523.3743 |  | 3046.7486 |  | 4900 | 16
1625.1171 |  | 3250.2342 |  | 4950 | 16
1757.2796 |  | 3514.5593 |  | 5000 | 16
1846.8509 |  | 3693.7017 |  | 5050 | 16
1914.581 |  | 3829.162 |  | 5100 | 16
1634.3829 |  | 3268.7658 |  | 5150 | 16
1915.2738 |  | 3830.5476 |  | 5200 | 16
2165.2718 |  | 4330.5437 |  | 5250 | 16
1914.1469 |  | 3828.2938 |  | 5300 | 16
2017.9874 |  | 4035.9748 |  | 5350 | 16
2141.5995 |  | 4283.199 |  | 5400 | 16
2290.5785 |  | 4581.157 |  | 5450 | 16
1727.4951 |  | 3454.9903 |  | 5500 | 16
1826.6982 |  | 3653.3965 |  | 5550 | 18
2003.3556 |  | 4006.7112 |  | 5600 | 18
2187.1986 |  | 4374.3972 |  | 5650 | 18
2293.6739 |  | 4587.3477 |  | 5700 | 18
2422.2984 |  | 4844.5968 |  | 5750 | 18
2547.3614 |  | 5094.7228 |  | 5800 | 18
2953.0528 |  | 5906.1056 |  | 5850 | 18
3220.9607 |  | 6441.9215 |  | 6000 | 18
3579.8797 |  | 7159.7593 |  | 6150 | 18
3926.8748 |  | 7853.7497 |  | 6300 | 18
4128.2784 |  | 8256.5567 |  | 6450 | 18
120.9035 |  | 362.7105 |  | 6600 | 18
134.1949 |  | 402.5848 |  | 6750 | 18
146.7341 |  | 440.2024 |  | 6900 | 18
154 |  | 462 |  | 7050 | 20
79 |  | 237 |  | 7200 | 20
169.9715 |  | 509.9146 |  | 7350 | 20
191.939 |  | 575.8169 |  | 7500 | 20
226.3257 |  | 678.977 |  | 7650 | 20
124.0691 |  | 372.2073 |  | 7800 | 20
190.191 |  | 570.5729 |  | 7950 | 20
214.0515 |  | 642.1546 |  | 8100 | 20
249.8523 |  | 749.5569 |  | 8250 | 20
243.9916 |  | 731.9747 |  | 8400 | 20
128.156 |  | 384.4681 |  | 8550 | 20
152.95 |  | 458.85 |  | 8700 | 20
168.2305 |  | 504.6915 |  | 8850 | 24
184.528 |  | 553.584 |  | 9000 | 24
191.32 |  | 573.96 |  | 9150 | 24
90.3291 |  | 270.9873 |  | 9300 | 24
95.22 |  | 285.66 |  | 9450 | 24
176.1225 |  | 528.3676 |  | 9600 | 24
200.368 |  | 601.1041 |  | 9750 | 24
232.5586 |  | 697.6759 |  | 9900 | 24
232.5586 |  | 697.6759 |  | 10050 | 24
111.4482 |  | 334.3446 |  | 10200 | 24
118.6369 |  | 355.9106 |  | 10350 | 24
205.3636 |  | 616.0908 |  | 10500 | 24
235.6474 |  | 706.9421 |  | 10650 | 24
257.4 |  | 772.2001 |  | 10800 | 24
277.4627 |  | 832.388 |  | 10950 | 24
300 |  | 900 |  | 11100 | 24
300 |  | 900 |  | 11250 | 24
136.1059 |  | 408.3177 |  | 11400 | 24
162.637 |  | 487.911 |  | 11550 | 24
165.3271 |  | 495.9813 |  | 11700 | 24
271.9533 |  | 815.8599 |  | 11850 | 24
309.3395 |  | 928.0185 |  | 12000 | 24
341.2848 |  | 1023.8543 |  | 12150 | 24
380.858 |  | 1142.5741 |  | 12300 | 24
405.1149 |  | 1215.3446 |  | 12450 | 24
406.8778 |  | 1220.6335 |  | 12600 | 24
154.2292 |  | 462.6875
205.8649 |  | 617.5946
227.7916 |  | 683.3749
294.5625 |  | 883.6876
355.8818 |  | 1067.6453
415.2757 |  | 1245.8272
449.14 |  | 1347.4201
222.9265 |  | 668.7796
339.6329 |  | 1018.8988
384.0902 |  | 1152.2706
424.5536 |  | 1273.6608
491.3603 |  | 1474.0808
551.7418 |  | 1655.2254
573.0512 |  | 1719.1537
179.981 |  | 539.9431
237.9031 |  | 713.7094
284.3868 |  | 853.1603
260.585 |  | 781.755
273.2839 |  | 819.8518
330.9972 |  | 992.9917
524.7552 |  | 1574.2657
534.9404 |  | 1604.8213
573.9449 |  | 1721.8346
599.7227 |  | 1799.168
512.3923 |  | 1537.1769
573.8168 |  | 1721.4503
630.1667 |  | 1890.5
681.695 |  | 2045.085
242.0702 |  | 726.2105
291.6367 |  | 874.91
290.4936 |  | 871.4809
350.6693 |  | 1052.008
375.4803 |  | 1126.4408
402.5638 |  | 1207.6913
427.3855 |  | 1282.1565
430.0891 |  | 1290.2674
453.84 |  | 1361.52
360.7205 |  | 1082.1614
391.3696 |  | 1174.1089
444.5377 |  | 1333.6131
455.5928 |  | 1366.7783
548.8465 |  | 1646.5396
628.8755 |  | 1886.6265
683.4996 |  | 2050.4988
734.2064 |  | 2202.6191
789.7994 |  | 2369.3983
360.84 |  | 1082.52
427.4383 |  | 1282.3149
913.8143 |  | 2741.443
969.4037 |  | 2908.2111
1015.343 |  | 3046.0289
1051.8577 |  | 3155.5731
1127.0937 |  | 3381.2812
456.5775 |  | 1369.7324
508.0798 |  | 1524.2394
534.9443 |  | 1604.833
568.82 |  | 1706.46
885.0742 |  | 2655.2225
912.6252 |  | 2737.8756
955.0129 |  | 2865.0386
1024.8269 |  | 3074.4806
1116.5838 |  | 3349.7514
466.2681 |  | 1398.8044
509.7501 |  | 1529.2504
543.4703 |  | 1630.411
607.7455 |  | 1823.2366
667.9 |  | 2003.7
732.8 |  | 2198.4
774.6 |  | 2323.8
813.5 |  | 2440.5
616.3385 |  | 1849.0154
707.5905 |  | 2122.7716
786.8099 |  | 2360.4297
825.5 |  | 2476.5
756.8 |  | 2270.4
830.5 |  | 2491.5
873.3 |  | 2619.9
639.1572 |  | 1917.4715
794.9133 |  | 2384.7399
882.342 |  | 2647.0261
935.9263 |  | 2807.7789
1136.2741 |  | 3408.8222
1332.9681 |  | 3998.9043
1528.3535 |  | 4585.0605
626.346 |  | 1879.0379
764.9699 |  | 2294.9098
682.0481 |  | 2046.1442
802.7921 |  | 2408.3762
932.9167 |  | 2798.7502
1000.0001 |  | 3000.0002
753.2463 |  | 2259.739
820.4429 |  | 2461.3287
953.3171 |  | 2859.9513
1029.7585 |  | 3089.2754
1330.3437 |  | 3991.0312
1378.5213 |  | 4135.5639
1467.9509 |  | 4403.8528
844.864 |  | 2534.5919
982.3526 |  | 2947.0578
1104.8611 |  | 3314.5834
1214.4257 |  | 3643.277
1383.6857 |  | 4151.0572
1551.2098 |  | 4653.6293
1664.6746 |  | 4994.0237
840.7876 |  | 2522.3627
995.4751 |  | 2986.4252
1093.6698 |  | 3281.0095
1144.8546 |  | 3434.5638
1204.5001 |  | 3613.5003
1252.5 |  | 3757.5
648.3835 |  | 1945.1505
820.3589 |  | 2461.0767
941.0352 |  | 2823.1056
1045.3157 |  | 3135.947
1136.5096 |  | 3409.5287
1235.933 |  | 3707.799
1229.0007 |  | 3687.0022
1303.9328 |  | 3911.7983
1403.874 |  | 4211.6221
1484.3188 |  | 4452.9564
1171.9065 |  | 3515.7196
1316.9347 |  | 3950.8041
1454.2378 |  | 4362.7133
1568.7217 |  | 4706.1651
1414.8836 |  | 4244.6507
1523.3743 |  | 4570.123
1625.1171 |  | 4875.3512
1757.2796 |  | 5271.8389
1846.8509 |  | 5540.5526
1914.581 |  | 5743.743
1634.3829 |  | 4903.1487
1915.2738 |  | 5745.8213
2165.2718 |  | 6495.8155
1914.1469 |  | 5742.4408
2017.9874 |  | 6053.9622
2141.5995 |  | 6424.7985
2290.5785 |  | 6871.7355
1727.4951 |  | 5182.4854
1826.6982 |  | 5480.0947
2003.3556 |  | 6010.0669
2187.1986 |  | 6561.5959
2293.6739 |  | 6881.0216
2422.2984 |  | 7266.8952
2547.3614 |  | 7642.0842
2953.0528 |  | 8859.1584
3220.9607 |  | 9662.8822
3579.8797 |  | 10739.639
3926.8748 |  | 11780.6245
4128.2784 |  | 12384.8351
120.9035 |  | 483.6139
134.1949 |  | 536.7797
146.7341 |  | 586.9365
154 |  | 616
79 |  | 316
169.9715 |  | 679.8862
191.939 |  | 767.7559
226.3257 |  | 905.3027
124.0691 |  | 496.2764
190.191 |  | 760.7639
214.0515 |  | 856.2061
249.8523 |  | 999.4092
243.9916 |  | 975.9663
128.156 |  | 512.6241
152.95 |  | 611.8001
168.2305 |  | 672.9221
184.528 |  | 738.1121
191.32 |  | 765.2801
90.3291 |  | 361.3164
95.22 |  | 380.88
176.1225 |  | 704.4902
200.368 |  | 801.4722
232.5586 |  | 930.2345
232.5586 |  | 930.2345
111.4482 |  | 445.7928
118.6369 |  | 474.5474
205.3636 |  | 821.4543
235.6474 |  | 942.5895
257.4 |  | 1029.6001
277.4627 |  | 1109.8506
300 |  | 1200
300 |  | 1200
136.1059 |  | 544.4236
162.637 |  | 650.548
165.3271 |  | 661.3083
271.9533 |  | 1087.8131
309.3395 |  | 1237.358
341.2848 |  | 1365.139
380.858 |  | 1523.4321
405.1149 |  | 1620.4594
406.8778 |  | 1627.5113
154.2292 |  | 616.9167
205.8649 |  | 823.4595
227.7916 |  | 911.1665
294.5625 |  | 1178.2501
355.8818 |  | 1423.5271
415.2757 |  | 1661.103
449.14 |  | 1796.5602
222.9265 |  | 891.7062
339.6329 |  | 1358.5317
384.0902 |  | 1536.3608
424.5536 |  | 1698.2144
491.3603 |  | 1965.4411
551.7418 |  | 2206.9672
573.0512 |  | 2292.2049
179.981 |  | 719.9241
237.9031 |  | 951.6126
284.3868 |  | 1137.547
260.585 |  | 1042.34
273.2839 |  | 1093.1357
330.9972 |  | 1323.9889
524.7552 |  | 2099.021
534.9404 |  | 2139.7617
573.9449 |  | 2295.7795
599.7227 |  | 2398.8907
512.3923 |  | 2049.5692
573.8168 |  | 2295.2671
630.1667 |  | 2520.6667
681.695 |  | 2726.78
242.0702 |  | 968.2806
291.6367 |  | 1166.5466
290.4936 |  | 1161.9746
350.6693 |  | 1402.6774
375.4803 |  | 1501.921
402.5638 |  | 1610.2551
427.3855 |  | 1709.542
430.0891 |  | 1720.3565
453.84 |  | 1815.36
360.7205 |  | 1442.8819
391.3696 |  | 1565.4785
444.5377 |  | 1778.1508
455.5928 |  | 1822.371
548.8465 |  | 2195.3862
628.8755 |  | 2515.502
683.4996 |  | 2733.9985
734.2064 |  | 2936.8255
789.7994 |  | 3159.1977
360.84 |  | 1443.36
427.4383 |  | 1709.7532
913.8143 |  | 3655.2573
969.4037 |  | 3877.6149
1015.343 |  | 4061.3719
1051.8577 |  | 4207.4307
1127.0937 |  | 4508.3749
456.5775 |  | 1826.3098
508.0798 |  | 2032.3192
534.9443 |  | 2139.7774
568.82 |  | 2275.28
885.0742 |  | 3540.2967
912.6252 |  | 3650.5009
955.0129 |  | 3820.0514
1024.8269 |  | 4099.3075
1116.5838 |  | 4466.3352
466.2681 |  | 1865.0725
509.7501 |  | 2039.0006
543.4703 |  | 2173.8813
607.7455 |  | 2430.9822
667.9 |  | 2671.6
732.8 |  | 2931.2
774.6 |  | 3098.4
813.5 |  | 3254
616.3385 |  | 2465.3539
707.5905 |  | 2830.3621
786.8099 |  | 3147.2397
825.5 |  | 3302
756.8 |  | 3027.2
830.5 |  | 3322
873.3 |  | 3493.2
639.1572 |  | 2556.6287
794.9133 |  | 3179.6532
882.342 |  | 3529.3682
935.9263 |  | 3743.7052
1136.2741 |  | 4545.0963
1332.9681 |  | 5331.8724
1528.3535 |  | 6113.414
626.346 |  | 2505.3838
764.9699 |  | 3059.8797
682.0481 |  | 2728.1922
802.7921 |  | 3211.1683
932.9167 |  | 3731.667
1000.0001 |  | 4000.0003
753.2463 |  | 3012.9853
820.4429 |  | 3281.7717
953.3171 |  | 3813.2684
1029.7585 |  | 4119.0339
1330.3437 |  | 5321.3749
1378.5213 |  | 5514.0852
1467.9509 |  | 5871.8037
844.864 |  | 3379.4558
982.3526 |  | 3929.4104
1104.8611 |  | 4419.4445
1214.4257 |  | 4857.7027
1383.6857 |  | 5534.743
1551.2098 |  | 6204.8391
1664.6746 |  | 6658.6983
840.7876 |  | 3363.1503
995.4751 |  | 3981.9003
1093.6698 |  | 4374.6794
1144.8546 |  | 4579.4184
1204.5001 |  | 4818.0004
1252.5 |  | 5010
648.3835 |  | 2593.534
820.3589 |  | 3281.4355
941.0352 |  | 3764.1408
1045.3157 |  | 4181.2627
1136.5096 |  | 4546.0383
1235.933 |  | 4943.7321
1229.0007 |  | 4916.0029
1303.9328 |  | 5215.731
1403.874 |  | 5615.4961
1484.3188 |  | 5937.2753
1171.9065 |  | 4687.6261
1316.9347 |  | 5267.7388
1454.2378 |  | 5816.9511
1568.7217 |  | 6274.8868
1414.8836 |  | 5659.5343
1523.3743 |  | 6093.4973
1625.1171 |  | 6500.4683
1757.2796 |  | 7029.1185
1846.8509 |  | 7387.4035
1914.581 |  | 7658.324
1634.3829 |  | 6537.5317
1915.2738 |  | 7661.0951
2165.2718 |  | 8661.0874
1914.1469 |  | 7656.5877
2017.9874 |  | 8071.9496
2141.5995 |  | 8566.398
2290.5785 |  | 9162.314
1727.4951 |  | 6909.9805
1826.6982 |  | 7306.7929
2003.3556 |  | 8013.4225
2187.1986 |  | 8748.7945
2293.6739 |  | 9174.6955
2422.2984 |  | 9689.1937
2547.3614 |  | 10189.4456
2953.0528 |  | 11812.2111
3220.9607 |  | 12883.8429
3579.8797 |  | 14319.5187
3926.8748 |  | 15707.4993
4128.2784 |  | 16513.1135
120.9035 |  | 120.9035
134.1949 |  | 134.1949
146.7341 |  | 146.7341
154 |  | 154
79 |  | 79
169.9715 |  | 169.9715
191.939 |  | 191.939
226.3257 |  | 226.3257
124.0691 |  | 124.0691
190.191 |  | 190.191
214.0515 |  | 214.0515
249.8523 |  | 249.8523
243.9916 |  | 243.9916
128.156 |  | 128.156
152.95 |  | 152.95
168.2305 |  | 168.2305
184.528 |  | 184.528
191.32 |  | 191.32
90.3291 |  | 90.3291
95.22 |  | 95.22
176.1225 |  | 176.1225
200.368 |  | 200.368
232.5586 |  | 232.5586
232.5586 |  | 232.5586
111.4482 |  | 111.4482
118.6369 |  | 118.6369
205.3636 |  | 205.3636
235.6474 |  | 235.6474
257.4 |  | 257.4
277.4627 |  | 277.4627
300 |  | 300
300 |  | 300
136.1059 |  | 136.1059
162.637 |  | 162.637
165.3271 |  | 165.3271
271.9533 |  | 271.9533
309.3395 |  | 309.3395
341.2848 |  | 341.2848
380.858 |  | 380.858
405.1149 |  | 405.1149
406.8778 |  | 406.8778
154.2292 |  | 154.2292
205.8649 |  | 205.8649
227.7916 |  | 227.7916
294.5625 |  | 294.5625
355.8818 |  | 355.8818
415.2757 |  | 415.2757
449.14 |  | 449.14
222.9265 |  | 222.9265
339.6329 |  | 339.6329
384.0902 |  | 384.0902
424.5536 |  | 424.5536
491.3603 |  | 491.3603
551.7418 |  | 551.7418
573.0512 |  | 573.0512
179.981 |  | 179.981
237.9031 |  | 237.9031
284.3868 |  | 284.3868
260.585 |  | 260.585
273.2839 |  | 273.2839
330.9972 |  | 330.9972
524.7552 |  | 524.7552
534.9404 |  | 534.9404
573.9449 |  | 573.9449
599.7227 |  | 599.7227
512.3923 |  | 512.3923
573.8168 |  | 573.8168
630.1667 |  | 630.1667
681.695 |  | 681.695
242.0702 |  | 242.0702
291.6367 |  | 291.6367
290.4936 |  | 290.4936
350.6693 |  | 350.6693
375.4803 |  | 375.4803
402.5638 |  | 402.5638
427.3855 |  | 427.3855
430.0891 |  | 430.0891
453.84 |  | 453.84
360.7205 |  | 360.7205
391.3696 |  | 391.3696
444.5377 |  | 444.5377
455.5928 |  | 455.5928
548.8465 |  | 548.8465
628.8755 |  | 628.8755
683.4996 |  | 683.4996
734.2064 |  | 734.2064
789.7994 |  | 789.7994
360.84 |  | 360.84
427.4383 |  | 427.4383
913.8143 |  | 913.8143
969.4037 |  | 969.4037
1015.343 |  | 1015.343
1051.8577 |  | 1051.8577
1127.0937 |  | 1127.0937
456.5775 |  | 456.5775
508.0798 |  | 508.0798
534.9443 |  | 534.9443
568.82 |  | 568.82
885.0742 |  | 885.0742
912.6252 |  | 912.6252
955.0129 |  | 955.0129
1024.8269 |  | 1024.8269
1116.5838 |  | 1116.5838
466.2681 |  | 466.2681
509.7501 |  | 509.7501
543.4703 |  | 543.4703
607.7455 |  | 607.7455
667.9 |  | 667.9
732.8 |  | 732.8
774.6 |  | 774.6
813.5 |  | 813.5
616.3385 |  | 616.3385
707.5905 |  | 707.5905
786.8099 |  | 786.8099
825.5 |  | 825.5
756.8 |  | 756.8
830.5 |  | 830.5
873.3 |  | 873.3
639.1572 |  | 639.1572
794.9133 |  | 794.9133
882.342 |  | 882.342
935.9263 |  | 935.9263
1136.2741 |  | 1136.2741
1332.9681 |  | 1332.9681
1528.3535 |  | 1528.3535
626.346 |  | 626.346
764.9699 |  | 764.9699
682.0481 |  | 682.0481
802.7921 |  | 802.7921
932.9167 |  | 932.9167
1000.0001 |  | 1000.0001
753.2463 |  | 753.2463
820.4429 |  | 820.4429
953.3171 |  | 953.3171
1029.7585 |  | 1029.7585
1330.3437 |  | 1330.3437
1378.5213 |  | 1378.5213
1467.9509 |  | 1467.9509
844.864 |  | 844.864
982.3526 |  | 982.3526
1104.8611 |  | 1104.8611
1214.4257 |  | 1214.4257
1383.6857 |  | 1383.6857
1551.2098 |  | 1551.2098
1664.6746 |  | 1664.6746
840.7876 |  | 840.7876
995.4751 |  | 995.4751
1093.6698 |  | 1093.6698
1144.8546 |  | 1144.8546
1204.5001 |  | 1204.5001
1252.5 |  | 1252.5
648.3835 |  | 648.3835
820.3589 |  | 820.3589
941.0352 |  | 941.0352
1045.3157 |  | 1045.3157
1136.5096 |  | 1136.5096
1235.933 |  | 1235.933
1229.0007 |  | 1229.0007
1303.9328 |  | 1303.9328
1403.874 |  | 1403.874
1484.3188 |  | 1484.3188
1171.9065 |  | 1171.9065
1316.9347 |  | 1316.9347
1454.2378 |  | 1454.2378
1568.7217 |  | 1568.7217
1414.8836 |  | 1414.8836
1523.3743 |  | 1523.3743
1625.1171 |  | 1625.1171
1757.2796 |  | 1757.2796
1846.8509 |  | 1846.8509
1914.581 |  | 1914.581
1634.3829 |  | 1634.3829
1915.2738 |  | 1915.2738
2165.2718 |  | 2165.2718
1914.1469 |  | 1914.1469
2017.9874 |  | 2017.9874
2141.5995 |  | 2141.5995
2290.5785 |  | 2290.5785
1727.4951 |  | 1727.4951
1826.6982 |  | 1826.6982
2003.3556 |  | 2003.3556
2187.1986 |  | 2187.1986
2293.6739 |  | 2293.6739
2422.2984 |  | 2422.2984
2547.3614 |  | 2547.3614
2953.0528 |  | 2953.0528
3220.9607 |  | 3220.9607
3579.8797 |  | 3579.8797
3926.8748 |  | 3926.8748
4128.2784 |  | 4128.2784
120.9035 |  | 241.807
134.1949 |  | 268.3898
146.7341 |  | 293.4682
154 |  | 308
79 |  | 158
169.9715 |  | 339.9431
191.939 |  | 383.8779
226.3257 |  | 452.6514
124.0691 |  | 248.1382
190.191 |  | 380.3819
214.0515 |  | 428.1031
249.8523 |  | 499.7046
243.9916 |  | 487.9832
128.156 |  | 256.3121
152.95 |  | 305.9
168.2305 |  | 336.461
184.528 |  | 369.056
191.32 |  | 382.64
90.3291 |  | 180.6582
95.22 |  | 190.44
176.1225 |  | 352.2451
200.368 |  | 400.7361
232.5586 |  | 465.1173
232.5586 |  | 465.1173
111.4482 |  | 222.8964
118.6369 |  | 237.2737
205.3636 |  | 410.7272
235.6474 |  | 471.2947
257.4 |  | 514.8
277.4627 |  | 554.9253
300 |  | 600
300 |  | 600
136.1059 |  | 272.2118
162.637 |  | 325.274
165.3271 |  | 330.6542
271.9533 |  | 543.9066
309.3395 |  | 618.679
341.2848 |  | 682.5695
380.858 |  | 761.716
405.1149 |  | 810.2297
406.8778 |  | 813.7556
154.2292 |  | 308.4583
205.8649 |  | 411.7298
227.7916 |  | 455.5833
294.5625 |  | 589.1251
355.8818 |  | 711.7636
415.2757 |  | 830.5515
449.14 |  | 898.2801
222.9265 |  | 445.8531
339.6329 |  | 679.2659
384.0902 |  | 768.1804
424.5536 |  | 849.1072
491.3603 |  | 982.7205
551.7418 |  | 1103.4836
573.0512 |  | 1146.1024
179.981 |  | 359.9621
237.9031 |  | 475.8063
284.3868 |  | 568.7735
260.585 |  | 521.17
273.2839 |  | 546.5679
330.9972 |  | 661.9944
524.7552 |  | 1049.5105
534.9404 |  | 1069.8809
573.9449 |  | 1147.8898
599.7227 |  | 1199.4453
512.3923 |  | 1024.7846
573.8168 |  | 1147.6336
630.1667 |  | 1260.3334
681.695 |  | 1363.39
242.0702 |  | 484.1403
291.6367 |  | 583.2733
290.4936 |  | 580.9873
350.6693 |  | 701.3387
375.4803 |  | 750.9605
402.5638 |  | 805.1276
427.3855 |  | 854.771
430.0891 |  | 860.1783
453.84 |  | 907.68
360.7205 |  | 721.4409
391.3696 |  | 782.7393
444.5377 |  | 889.0754
455.5928 |  | 911.1855
548.8465 |  | 1097.6931
628.8755 |  | 1257.751
683.4996 |  | 1366.9992
734.2064 |  | 1468.4128
789.7994 |  | 1579.5988
360.84 |  | 721.68
427.4383 |  | 854.8766
913.8143 |  | 1827.6287
969.4037 |  | 1938.8074
1015.343 |  | 2030.6859
1051.8577 |  | 2103.7154
1127.0937 |  | 2254.1875
456.5775 |  | 913.1549
508.0798 |  | 1016.1596
534.9443 |  | 1069.8887
568.82 |  | 1137.64
885.0742 |  | 1770.1484
912.6252 |  | 1825.2504
955.0129 |  | 1910.0257
1024.8269 |  | 2049.6538
1116.5838 |  | 2233.1676
466.2681 |  | 932.5363
509.7501 |  | 1019.5003
543.4703 |  | 1086.9406
607.7455 |  | 1215.4911
667.9 |  | 1335.8
732.8 |  | 1465.6
774.6 |  | 1549.2
813.5 |  | 1627
616.3385 |  | 1232.6769
707.5905 |  | 1415.1811
786.8099 |  | 1573.6198
825.5 |  | 1651
756.8 |  | 1513.6
830.5 |  | 1661
873.3 |  | 1746.6
639.1572 |  | 1278.3144
794.9133 |  | 1589.8266
882.342 |  | 1764.6841
935.9263 |  | 1871.8526
1136.2741 |  | 2272.5482
1332.9681 |  | 2665.9362
1528.3535 |  | 3056.707
626.346 |  | 1252.6919
764.9699 |  | 1529.9399
682.0481 |  | 1364.0961
802.7921 |  | 1605.5841
932.9167 |  | 1865.8335
1000.0001 |  | 2000.0002
753.2463 |  | 1506.4926
820.4429 |  | 1640.8858
953.3171 |  | 1906.6342
1029.7585 |  | 2059.5169
1330.3437 |  | 2660.6874
1378.5213 |  | 2757.0426
1467.9509 |  | 2935.9018
844.864 |  | 1689.7279
982.3526 |  | 1964.7052
1104.8611 |  | 2209.7222
1214.4257 |  | 2428.8514
1383.6857 |  | 2767.3715
1551.2098 |  | 3102.4196
1664.6746 |  | 3329.3491
840.7876 |  | 1681.5751
995.4751 |  | 1990.9502
1093.6698 |  | 2187.3397
1144.8546 |  | 2289.7092
1204.5001 |  | 2409.0002
1252.5 |  | 2505
648.3835 |  | 1296.767
820.3589 |  | 1640.7178
941.0352 |  | 1882.0704
1045.3157 |  | 2090.6314
1136.5096 |  | 2273.0192
1235.933 |  | 2471.866
1229.0007 |  | 2458.0014
1303.9328 |  | 2607.8655
1403.874 |  | 2807.748
1484.3188 |  | 2968.6376
1171.9065 |  | 2343.8131
1316.9347 |  | 2633.8694
1454.2378 |  | 2908.4756
1568.7217 |  | 3137.4434
1414.8836 |  | 2829.7672
1523.3743 |  | 3046.7486
1625.1171 |  | 3250.2342
1757.2796 |  | 3514.5593
1846.8509 |  | 3693.7017
1914.581 |  | 3829.162
1634.3829 |  | 3268.7658
1915.2738 |  | 3830.5476
2165.2718 |  | 4330.5437
1914.1469 |  | 3828.2938
2017.9874 |  | 4035.9748
2141.5995 |  | 4283.199
2290.5785 |  | 4581.157
1727.4951 |  | 3454.9903
1826.6982 |  | 3653.3965
2003.3556 |  | 4006.7112
2187.1986 |  | 4374.3972
2293.6739 |  | 4587.3477
2422.2984 |  | 4844.5968
2547.3614 |  | 5094.7228
2953.0528 |  | 5906.1056
3220.9607 |  | 6441.9215
3579.8797 |  | 7159.7593
3926.8748 |  | 7853.7497
4128.2784 |  | 8256.5567
120.9035 |  | 362.7105
134.1949 |  | 402.5848
146.7341 |  | 440.2024
154 |  | 462
79 |  | 237
169.9715 |  | 509.9146
191.939 |  | 575.8169
226.3257 |  | 678.977
124.0691 |  | 372.2073
190.191 |  | 570.5729
214.0515 |  | 642.1546
249.8523 |  | 749.5569
243.9916 |  | 731.9747
128.156 |  | 384.4681
152.95 |  | 458.85
168.2305 |  | 504.6915
184.528 |  | 553.584
191.32 |  | 573.96
90.3291 |  | 270.9873
95.22 |  | 285.66
176.1225 |  | 528.3676
200.368 |  | 601.1041
232.5586 |  | 697.6759
232.5586 |  | 697.6759
111.4482 |  | 334.3446
118.6369 |  | 355.9106
205.3636 |  | 616.0908
235.6474 |  | 706.9421
257.4 |  | 772.2001
277.4627 |  | 832.388
300 |  | 900
300 |  | 900
136.1059 |  | 408.3177
162.637 |  | 487.911
165.3271 |  | 495.9813
271.9533 |  | 815.8599
309.3395 |  | 928.0185
341.2848 |  | 1023.8543
380.858 |  | 1142.5741
405.1149 |  | 1215.3446
406.8778 |  | 1220.6335
154.2292 |  | 462.6875
205.8649 |  | 617.5946
227.7916 |  | 683.3749
294.5625 |  | 883.6876
355.8818 |  | 1067.6453
415.2757 |  | 1245.8272
449.14 |  | 1347.4201
222.9265 |  | 668.7796
339.6329 |  | 1018.8988
384.0902 |  | 1152.2706
424.5536 |  | 1273.6608
491.3603 |  | 1474.0808
551.7418 |  | 1655.2254
573.0512 |  | 1719.1537
179.981 |  | 539.9431
237.9031 |  | 713.7094
284.3868 |  | 853.1603
260.585 |  | 781.755
273.2839 |  | 819.8518
330.9972 |  | 992.9917
524.7552 |  | 1574.2657
534.9404 |  | 1604.8213
573.9449 |  | 1721.8346
599.7227 |  | 1799.168
512.3923 |  | 1537.1769
573.8168 |  | 1721.4503
630.1667 |  | 1890.5
681.695 |  | 2045.085
242.0702 |  | 726.2105
291.6367 |  | 874.91
290.4936 |  | 871.4809
350.6693 |  | 1052.008
375.4803 |  | 1126.4408
402.5638 |  | 1207.6913
427.3855 |  | 1282.1565
430.0891 |  | 1290.2674
453.84 |  | 1361.52
360.7205 |  | 1082.1614
391.3696 |  | 1174.1089
444.5377 |  | 1333.6131
455.5928 |  | 1366.7783
548.8465 |  | 1646.5396
628.8755 |  | 1886.6265
683.4996 |  | 2050.4988
734.2064 |  | 2202.6191
789.7994 |  | 2369.3983
360.84 |  | 1082.52
427.4383 |  | 1282.3149
913.8143 |  | 2741.443
969.4037 |  | 2908.2111
1015.343 |  | 3046.0289
1051.8577 |  | 3155.5731
1127.0937 |  | 3381.2812
456.5775 |  | 1369.7324
508.0798 |  | 1524.2394
534.9443 |  | 1604.833
568.82 |  | 1706.46
885.0742 |  | 2655.2225
912.6252 |  | 2737.8756
955.0129 |  | 2865.0386
1024.8269 |  | 3074.4806
1116.5838 |  | 3349.7514
466.2681 |  | 1398.8044
509.7501 |  | 1529.2504
543.4703 |  | 1630.411
607.7455 |  | 1823.2366
667.9 |  | 2003.7
732.8 |  | 2198.4
774.6 |  | 2323.8
813.5 |  | 2440.5
616.3385 |  | 1849.0154
707.5905 |  | 2122.7716
786.8099 |  | 2360.4297
825.5 |  | 2476.5
756.8 |  | 2270.4
830.5 |  | 2491.5
873.3 |  | 2619.9
639.1572 |  | 1917.4715
794.9133 |  | 2384.7399
882.342 |  | 2647.0261
935.9263 |  | 2807.7789
1136.2741 |  | 3408.8222
1332.9681 |  | 3998.9043
1528.3535 |  | 4585.0605
626.346 |  | 1879.0379
764.9699 |  | 2294.9098
682.0481 |  | 2046.1442
802.7921 |  | 2408.3762
932.9167 |  | 2798.7502
1000.0001 |  | 3000.0002
753.2463 |  | 2259.739
820.4429 |  | 2461.3287
953.3171 |  | 2859.9513
1029.7585 |  | 3089.2754
1330.3437 |  | 3991.0312
1378.5213 |  | 4135.5639
1467.9509 |  | 4403.8528
844.864 |  | 2534.5919
982.3526 |  | 2947.0578
1104.8611 |  | 3314.5834
1214.4257 |  | 3643.277
1383.6857 |  | 4151.0572
1551.2098 |  | 4653.6293
1664.6746 |  | 4994.0237
840.7876 |  | 2522.3627
995.4751 |  | 2986.4252
1093.6698 |  | 3281.0095
1144.8546 |  | 3434.5638
1204.5001 |  | 3613.5003
1252.5 |  | 3757.5
648.3835 |  | 1945.1505
820.3589 |  | 2461.0767
941.0352 |  | 2823.1056
1045.3157 |  | 3135.947
1136.5096 |  | 3409.5287
1235.933 |  | 3707.799
1229.0007 |  | 3687.0022
1303.9328 |  | 3911.7983
1403.874 |  | 4211.6221
1484.3188 |  | 4452.9564
1171.9065 |  | 3515.7196
1316.9347 |  | 3950.8041
1454.2378 |  | 4362.7133
1568.7217 |  | 4706.1651
1414.8836 |  | 4244.6507
1523.3743 |  | 4570.123
1625.1171 |  | 4875.3512
1757.2796 |  | 5271.8389
1846.8509 |  | 5540.5526
1914.581 |  | 5743.743
1634.3829 |  | 4903.1487
1915.2738 |  | 5745.8213
2165.2718 |  | 6495.8155
1914.1469 |  | 5742.4408
2017.9874 |  | 6053.9622
2141.5995 |  | 6424.7985
2290.5785 |  | 6871.7355
1727.4951 |  | 5182.4854
1826.6982 |  | 5480.0947
2003.3556 |  | 6010.0669
2187.1986 |  | 6561.5959
2293.6739 |  | 6881.0216
2422.2984 |  | 7266.8952
2547.3614 |  | 7642.0842
2953.0528 |  | 8859.1584
3220.9607 |  | 9662.8822
3579.8797 |  | 10739.639
3926.8748 |  | 11780.6245
4128.2784 |  | 12384.8351
120.9035 |  | 483.6139
134.1949 |  | 536.7797
146.7341 |  | 586.9365
154 |  | 616
79 |  | 316
169.9715 |  | 679.8862
191.939 |  | 767.7559
226.3257 |  | 905.3027
124.0691 |  | 496.2764
190.191 |  | 760.7639
214.0515 |  | 856.2061
249.8523 |  | 999.4092
243.9916 |  | 975.9663
128.156 |  | 512.6241
152.95 |  | 611.8001
168.2305 |  | 672.9221
184.528 |  | 738.1121
191.32 |  | 765.2801
90.3291 |  | 361.3164
95.22 |  | 380.88
176.1225 |  | 704.4902
200.368 |  | 801.4722
232.5586 |  | 930.2345
232.5586 |  | 930.2345
111.4482 |  | 445.7928
118.6369 |  | 474.5474
205.3636 |  | 821.4543
235.6474 |  | 942.5895
257.4 |  | 1029.6001
277.4627 |  | 1109.8506
300 |  | 1200
300 |  | 1200
136.1059 |  | 544.4236
162.637 |  | 650.548
165.3271 |  | 661.3083
271.9533 |  | 1087.8131
309.3395 |  | 1237.358
341.2848 |  | 1365.139
380.858 |  | 1523.4321
405.1149 |  | 1620.4594
406.8778 |  | 1627.5113
154.2292 |  | 616.9167
205.8649 |  | 823.4595
227.7916 |  | 911.1665
294.5625 |  | 1178.2501
355.8818 |  | 1423.5271
415.2757 |  | 1661.103
449.14 |  | 1796.5602
222.9265 |  | 891.7062
339.6329 |  | 1358.5317
384.0902 |  | 1536.3608
424.5536 |  | 1698.2144
491.3603 |  | 1965.4411
551.7418 |  | 2206.9672
573.0512 |  | 2292.2049
179.981 |  | 719.9241
237.9031 |  | 951.6126
284.3868 |  | 1137.547
260.585 |  | 1042.34
273.2839 |  | 1093.1357
330.9972 |  | 1323.9889
524.7552 |  | 2099.021
534.9404 |  | 2139.7617
573.9449 |  | 2295.7795
599.7227 |  | 2398.8907
512.3923 |  | 2049.5692
573.8168 |  | 2295.2671
630.1667 |  | 2520.6667
681.695 |  | 2726.78
242.0702 |  | 968.2806
291.6367 |  | 1166.5466
290.4936 |  | 1161.9746
350.6693 |  | 1402.6774
375.4803 |  | 1501.921
402.5638 |  | 1610.2551
427.3855 |  | 1709.542
430.0891 |  | 1720.3565
453.84 |  | 1815.36
360.7205 |  | 1442.8819
391.3696 |  | 1565.4785
444.5377 |  | 1778.1508
455.5928 |  | 1822.371
548.8465 |  | 2195.3862
628.8755 |  | 2515.502
683.4996 |  | 2733.9985
734.2064 |  | 2936.8255
789.7994 |  | 3159.1977
360.84 |  | 1443.36
427.4383 |  | 1709.7532
913.8143 |  | 3655.2573
969.4037 |  | 3877.6149
1015.343 |  | 4061.3719
1051.8577 |  | 4207.4307
1127.0937 |  | 4508.3749
456.5775 |  | 1826.3098
508.0798 |  | 2032.3192
534.9443 |  | 2139.7774
568.82 |  | 2275.28
885.0742 |  | 3540.2967
912.6252 |  | 3650.5009
955.0129 |  | 3820.0514
1024.8269 |  | 4099.3075
1116.5838 |  | 4466.3352
466.2681 |  | 1865.0725
509.7501 |  | 2039.0006
543.4703 |  | 2173.8813
607.7455 |  | 2430.9822
667.9 |  | 2671.6
732.8 |  | 2931.2
774.6 |  | 3098.4
813.5 |  | 3254
616.3385 |  | 2465.3539
707.5905 |  | 2830.3621
786.8099 |  | 3147.2397
825.5 |  | 3302
756.8 |  | 3027.2
830.5 |  | 3322
873.3 |  | 3493.2
639.1572 |  | 2556.6287
794.9133 |  | 3179.6532
882.342 |  | 3529.3682
935.9263 |  | 3743.7052
1136.2741 |  | 4545.0963
1332.9681 |  | 5331.8724
1528.3535 |  | 6113.414
626.346 |  | 2505.3838
764.9699 |  | 3059.8797
682.0481 |  | 2728.1922
802.7921 |  | 3211.1683
932.9167 |  | 3731.667
1000.0001 |  | 4000.0003
753.2463 |  | 3012.9853
820.4429 |  | 3281.7717
953.3171 |  | 3813.2684
1029.7585 |  | 4119.0339
1330.3437 |  | 5321.3749
1378.5213 |  | 5514.0852
1467.9509 |  | 5871.8037
844.864 |  | 3379.4558
982.3526 |  | 3929.4104
1104.8611 |  | 4419.4445
1214.4257 |  | 4857.7027
1383.6857 |  | 5534.743
1551.2098 |  | 6204.8391
1664.6746 |  | 6658.6983
840.7876 |  | 3363.1503
995.4751 |  | 3981.9003
1093.6698 |  | 4374.6794
1144.8546 |  | 4579.4184
1204.5001 |  | 4818.0004
1252.5 |  | 5010
648.3835 |  | 2593.534
820.3589 |  | 3281.4355
941.0352 |  | 3764.1408
1045.3157 |  | 4181.2627
1136.5096 |  | 4546.0383
1235.933 |  | 4943.7321
1229.0007 |  | 4916.0029
1303.9328 |  | 5215.731
1403.874 |  | 5615.4961
1484.3188 |  | 5937.2753
1171.9065 |  | 4687.6261
1316.9347 |  | 5267.7388
1454.2378 |  | 5816.9511
1568.7217 |  | 6274.8868
1414.8836 |  | 5659.5343
1523.3743 |  | 6093.4973
1625.1171 |  | 6500.4683
1757.2796 |  | 7029.1185
1846.8509 |  | 7387.4035
1914.581 |  | 7658.324
1634.3829 |  | 6537.5317
1915.2738 |  | 7661.0951
2165.2718 |  | 8661.0874
1914.1469 |  | 7656.5877
2017.9874 |  | 8071.9496
2141.5995 |  | 8566.398
2290.5785 |  | 9162.314
1727.4951 |  | 6909.9805
1826.6982 |  | 7306.7929
2003.3556 |  | 8013.4225
2187.1986 |  | 8748.7945
2293.6739 |  | 9174.6955
2422.2984 |  | 9689.1937
2547.3614 |  | 10189.4456
2953.0528 |  | 11812.2111
3220.9607 |  | 12883.8429
3579.8797 |  | 14319.5187
3926.8748 |  | 15707.4993
4128.2784 |  | 16513.1135