## GES_NBSE
Sequencing | Pump Size ID | Pump Size | Curve | Max flow @ max speed (gpm), 1 pump | Max Branch Flow | Max Header Flow | Number of Active Pumps | Number of Backup Pumps | Number of Total Pumps | Cost Group | Cost Group Type | Suction | Discharge | Branch Minimum | Branch Maximum | Header Minimum | Header Maximum
1 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 494.9704 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
2 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 327.1054 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
3 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 367.1458 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
4 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 562.5574 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
5 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 593.5193 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
6 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 637.7298 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
7 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 726.789 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
8 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 888.3994 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
9 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 708.3921 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
10 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 739.6035 | 2 | 0 | 2 | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
11 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 699.8896 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
12 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 840.7716 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
13 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 977.1333 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
14 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 1043.9688 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
15 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 1011.2506 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
16 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 1148.6886 | 2 | 0 | 2 | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
17 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 1558.7406 | 2 | 0 | 2 | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
18 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 1656.7734 | 2 | 0 | 2 | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
19 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 1470.5969 | 2 | 0 | 2 | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
20 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 1699.5167 | 2 | 0 | 2 | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
21 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 1770.2267 | 2 | 0 | 2 | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
22 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 1706.1572 | 2 | 0 | 2 | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
23 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 1970.7665 | 2 | 0 | 2 | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
24 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 2218.1669 | 2 | 0 | 2 | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
25 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 2452.6065 | 2 | 0 | 2 | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
26 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 2701.649 | 2 | 0 | 2 | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
27 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 742.4556 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
28 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 490.658 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
29 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 550.7188 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
30 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 843.8361 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
31 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 890.2789 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
32 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 956.5946 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
33 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 1090.1836 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
34 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 1332.5991 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
35 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 1062.5881 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
36 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 1109.4052 | 3 | 0 | 3 | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
37 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 1049.8344 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
38 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 1261.1574 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
39 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 1465.7 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
40 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 1565.9533 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
41 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 1516.876 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
42 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 1723.0329 | 3 | 0 | 3 | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
43 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 2338.1109 | 3 | 0 | 3 | B | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
44 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 2485.1601 | 3 | 0 | 3 | B | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
45 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 2205.8954 | 3 | 0 | 3 | B | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
46 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 2549.275 | 3 | 0 | 3 | B | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
47 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 2655.3401 | 3 | 0 | 3 | B | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
48 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 2559.2358 | 3 | 0 | 3 | B | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
49 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 2956.1497 | 3 | 0 | 3 | B | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
50 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 3327.2504 | 3 | 0 | 3 | B | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
51 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 3678.9097 | 3 | 0 | 3 | B | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
52 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 4052.4735 | 3 | 0 | 3 | B | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
53 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 989.9408 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
54 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 654.2107 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
55 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 734.2917 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
56 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 1125.1148 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
57 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 1187.0386 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
58 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 1275.4595 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
59 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 1453.5781 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
60 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 1776.7988 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
61 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 1416.7841 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
62 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 1479.207 | 4 | 0 | 4 | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
63 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 1399.7792 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
64 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 1681.5432 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
65 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 1954.2666 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
66 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 2087.9377 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
67 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 2022.5013 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
68 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 2297.3772 | 4 | 0 | 4 | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
69 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 3117.4812 | 4 | 0 | 4 | C | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
70 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 3313.5469 | 4 | 0 | 4 | C | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
71 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 2941.1939 | 4 | 0 | 4 | C | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
72 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 3399.0334 | 4 | 0 | 4 | C | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
73 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 3540.4535 | 4 | 0 | 4 | C | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
74 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 3412.3143 | 4 | 0 | 4 | C | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
75 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 3941.533 | 4 | 0 | 4 | C | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
76 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 4436.3339 | 4 | 0 | 4 | C | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
77 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 4905.2129 | 4 | 0 | 4 | C | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
78 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 5403.298 | 4 | 0 | 4 | C | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
79 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 247.4852 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
80 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 163.5527 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
81 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 183.5729 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
82 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 281.2787 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
83 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 296.7596 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
84 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 318.8649 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
85 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 363.3945 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
86 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 444.1997 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
87 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 354.196 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
88 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 369.8017 | 1 | 1 | 2 | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
89 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 349.9448 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
90 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 420.3858 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
91 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 488.5667 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
92 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 521.9844 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
93 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 505.6253 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
94 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 574.3443 | 1 | 1 | 2 | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
95 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 779.3703 | 1 | 1 | 2 | D | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
96 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 828.3867 | 1 | 1 | 2 | D | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
97 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 735.2985 | 1 | 1 | 2 | D | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
98 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 849.7583 | 1 | 1 | 2 | D | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
99 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 885.1134 | 1 | 1 | 2 | D | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
100 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 853.0786 | 1 | 1 | 2 | D | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
101 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 985.3832 | 1 | 1 | 2 | D | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
102 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 1109.0835 | 1 | 1 | 2 | D | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
103 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 1226.3032 | 1 | 1 | 2 | D | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
104 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 1350.8245 | 1 | 1 | 2 | D | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
105 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 494.9704 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
106 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 327.1054 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
107 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 367.1458 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
108 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 562.5574 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
109 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 593.5193 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
110 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 637.7298 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
111 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 726.789 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
112 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 888.3994 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
113 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 708.3921 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
114 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 739.6035 | 2 | 1 | 3 | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
115 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 699.8896 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
116 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 840.7716 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
117 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 977.1333 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
118 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 1043.9688 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
119 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 1011.2506 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
120 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 1148.6886 | 2 | 1 | 3 | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
121 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 1558.7406 | 2 | 1 | 3 | E | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
122 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 1656.7734 | 2 | 1 | 3 | E | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
123 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 1470.5969 | 2 | 1 | 3 | E | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
124 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 1699.5167 | 2 | 1 | 3 | E | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
125 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 1770.2267 | 2 | 1 | 3 | E | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
126 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 1706.1572 | 2 | 1 | 3 | E | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
127 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 1970.7665 | 2 | 1 | 3 | E | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
128 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 2218.1669 | 2 | 1 | 3 | E | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
129 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 2452.6065 | 2 | 1 | 3 | E | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
130 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 2701.649 | 2 | 1 | 3 | E | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
131 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 742.4556 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
132 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 490.658 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
133 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 550.7188 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
134 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 843.8361 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
135 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 890.2789 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
136 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 956.5946 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
137 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 1090.1836 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
138 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 1332.5991 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
139 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 1062.5881 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
140 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 1109.4052 | 3 | 1 | 4 | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
141 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 1049.8344 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
142 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 1261.1574 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
143 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 1465.7 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
144 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 1565.9533 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
145 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 1516.876 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
146 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 1723.0329 | 3 | 1 | 4 | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
147 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 2338.1109 | 3 | 1 | 4 | F | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
148 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 2485.1601 | 3 | 1 | 4 | F | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
149 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 2205.8954 | 3 | 1 | 4 | F | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
150 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 2549.275 | 3 | 1 | 4 | F | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
151 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 2655.3401 | 3 | 1 | 4 | F | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
152 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 2559.2358 | 3 | 1 | 4 | F | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
153 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 2956.1497 | 3 | 1 | 4 | F | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
154 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 3327.2504 | 3 | 1 | 4 | F | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
155 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 3678.9097 | 3 | 1 | 4 | F | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
156 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 4052.4735 | 3 | 1 | 4 | F | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858
157 | 1 | 015-070-4P-3HP | 015-070-4P-D176-3HP-E | 247.4852 | 247.4852 | 989.9408 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D119-3HP-E | 137.956
158 | 2 | 015-090-4P-3HP | 015-090-4P-D206-3HP-E | 163.5527 | 163.5527 | 654.2107 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D127-5HP-E | 146.2341
159 | 3 | 015-090-4P-5HP | 015-090-4P-D250-5HP-E | 183.5729 | 183.5729 | 734.2917 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D139-7.5HP-E | 166.571
160 | 4 | 015-095-4P-5HP | 015-095-4P-D224-5HP-E | 281.2787 | 281.2787 | 1125.1148 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D155-7.5HP-E | 198.4696
161 | 5 | 015-095-4P-7pt5HP | 015-095-4P-D250-7.5HP-E | 296.7596 | 296.7596 | 1187.0386 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 012-070-2P-D163-10HP-E | 209.9648
162 | 6 | 020-095-4P-5HP | 020-095-4P-D206-5HP-E | 318.8649 | 318.8649 | 1275.4595 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D169-15HP-E | 219.9434
163 | 7 | 020-095-4P-7pt5HP | 020-095-4P-D240-7.5HP-E | 363.3945 | 363.3945 | 1453.5781 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 012-070-2P-D177-15HP-E | 224.2633
164 | 8 | 020-110-4P-10HP | 020-110-4P-D252-10HP-E | 444.1997 | 444.1997 | 1776.7988 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D114-5HP-E | 264.8569
165 | 9 | 025-070-4P-3HP | 025-070-4P-D168-3HP-E | 354.196 | 354.196 | 1416.7841 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D128-7.5HP-E | 310.9403
166 | 10 | 025-070-4P-5HP | 025-070-4P-D172-5HP-E | 369.8017 | 369.8017 | 1479.207 | 4 | 1 | 5 | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  | 015-070-2P-D142-10HP-E | 342.592
167 | 11 | 025-095-4P-3HP | 025-095-4P-D152-3HP-E | 349.9448 | 349.9448 | 1399.7792 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-2P-D160-15HP-E | 387.697
168 | 12 | 025-095-4P-5HP | 025-095-4P-D182-5HP-E | 420.3858 | 420.3858 | 1681.5432 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-070-4P-D176-3HP-E | 247.4852
169 | 13 | 025-095-4P-7pt5HP | 025-095-4P-D214-7.5HP-E | 488.5667 | 488.5667 | 1954.2666 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D206-3HP-E | 163.5527
170 | 14 | 025-095-4P-10HP | 025-095-4P-D242-10HP-E | 521.9844 | 521.9844 | 2087.9377 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-090-4P-D250-5HP-E | 183.5729
171 | 15 | 030-070-4P-3HP | 030-070-4P-D148-3HP-E | 505.6253 | 505.6253 | 2022.5013 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D224-5HP-E | 281.2787
172 | 16 | 030-070-4P-5HP | 030-070-4P-D174-5HP-E | 574.3443 | 574.3443 | 2297.3772 | 4 | 1 | 5 | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  | 015-095-4P-D250-7.5HP-E | 296.7596
173 | 17 | 030-095-4P-7pt5HP | 030-095-4P-D171-7.5HP-E | 779.3703 | 779.3703 | 3117.4812 | 4 | 1 | 5 | G | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D206-5HP-E | 318.8649
174 | 18 | 030-095-4P-10HP | 030-095-4P-D191-10HP-E | 828.3867 | 828.3867 | 3313.5469 | 4 | 1 | 5 | G | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-095-4P-D240-7.5HP-E | 363.3945
175 | 19 | 040-070-4P-3HP | 040-070-4P-D138-3HP-E | 735.2985 | 735.2985 | 2941.1939 | 4 | 1 | 5 | G | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 020-110-4P-D252-10HP-E | 444.1997
176 | 20 | 040-070-4P-5HP | 040-070-4P-D160-5HP-E | 849.7583 | 849.7583 | 3399.0334 | 4 | 1 | 5 | G | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D116-7.5HP-E | 423.3602
177 | 21 | 040-070-4P-7pt5HP | 040-070-4P-D174-7.5HP-E | 885.1134 | 885.1134 | 3540.4535 | 4 | 1 | 5 | G | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  | 025-070-2P-D126-10HP-E | 481.8205
178 | 22 | 050-070-4P-3HP | 050-070-4P-D124-3HP-E | 853.0786 | 853.0786 | 3412.3143 | 4 | 1 | 5 | G | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-2P-D144-15HP-E | 558.3815
179 | 23 | 050-070-4P-5HP | 050-070-4P-D154-5HP-E | 985.3832 | 985.3832 | 3941.533 | 4 | 1 | 5 | G | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D168-3HP-E | 354.196
180 | 24 | 050-070-4P-7pt5HP | 050-070-4P-D168-7.5HP-E | 1109.0835 | 1109.0835 | 4436.3339 | 4 | 1 | 5 | G | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-070-4P-D172-5HP-E | 369.8017
181 | 25 | 050-070-4P-10HP | 050-070-4P-D176-10HP-E | 1226.3032 | 1226.3032 | 4905.2129 | 4 | 1 | 5 | G | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  | 025-095-4P-D152-3HP-E | 349.9448
182 | 26 | 050-095-4P-10HP | 050-095-4P-D164-10HP-E | 1350.8245 | 1350.8245 | 5403.298 | 4 | 1 | 5 | G | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  | 025-095-4P-D182-5HP-E | 420.3858

## Max flow to diameter
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.) | Flow (gpm) | Pipe Diameter (in.)
247.4852 | 4 | 494.9704 | 5 | 20 | 2
163.5527 | 3 | 327.1054 | 4 | 25 | 2
183.5729 |  | 367.1458 |  | 30 | 2
281.2787 |  | 562.5574 |  | 35 | 2
296.7596 |  | 593.5193 |  | 40 | 2
318.8649 |  | 637.7298 |  | 45 | 2
363.3945 |  | 726.789 |  | 50 | 2
444.1997 |  | 888.3994 |  | 55 | 2
354.196 |  | 708.3921 |  | 60 | 2
369.8017 |  | 739.6035 |  | 65 | 2
349.9448 |  | 699.8896 |  | 70 | 2
420.3858 |  | 840.7716 |  | 75 | 2
488.5667 |  | 977.1333 |  | 80 | 2
521.9844 |  | 1043.9688 |  | 85 | 2.5
505.6253 |  | 1011.2506 |  | 90 | 2.5
574.3443 |  | 1148.6886 |  | 95 | 2.5
779.3703 |  | 1558.7406 |  | 100 | 2.5
828.3867 |  | 1656.7734 |  | 105 | 2.5
735.2985 |  | 1470.5969 |  | 110 | 2.5
849.7583 |  | 1699.5167 |  | 115 | 2.5
885.1134 |  | 1770.2267 |  | 120 | 2.5
853.0786 |  | 1706.1572 |  | 125 | 3
985.3832 |  | 1970.7665 |  | 130 | 3
1109.0835 |  | 2218.1669 |  | 135 | 3
1226.3032 |  | 2452.6065 |  | 140 | 3
1350.8245 |  | 2701.649 |  | 145 | 3
247.4852 |  | 742.4556 |  | 150 | 3
163.5527 |  | 490.658 |  | 155 | 3
183.5729 |  | 550.7188 |  | 160 | 3
281.2787 |  | 843.8361 |  | 165 | 3
296.7596 |  | 890.2789 |  | 170 | 3
318.8649 |  | 956.5946 |  | 175 | 3
363.3945 |  | 1090.1836 |  | 180 | 3
444.1997 |  | 1332.5991 |  | 185 | 3
354.196 |  | 1062.5881 |  | 190 | 3
369.8017 |  | 1109.4052 |  | 195 | 3
349.9448 |  | 1049.8344 |  | 200 | 3
420.3858 |  | 1261.1574 |  | 205 | 3
488.5667 |  | 1465.7 |  | 210 | 3
521.9844 |  | 1565.9533 |  | 215 | 4
505.6253 |  | 1516.876 |  | 220 | 4
574.3443 |  | 1723.0329 |  | 225 | 4
779.3703 |  | 2338.1109 |  | 230 | 4
828.3867 |  | 2485.1601 |  | 235 | 4
735.2985 |  | 2205.8954 |  | 240 | 4
849.7583 |  | 2549.275 |  | 245 | 4
885.1134 |  | 2655.3401 |  | 250 | 4
853.0786 |  | 2559.2358 |  | 255 | 4
985.3832 |  | 2956.1497 |  | 260 | 4
1109.0835 |  | 3327.2504 |  | 265 | 4
1226.3032 |  | 3678.9097 |  | 270 | 4
1350.8245 |  | 4052.4735 |  | 275 | 4
247.4852 |  | 989.9408 |  | 280 | 4
163.5527 |  | 654.2107 |  | 285 | 4
183.5729 |  | 734.2917 |  | 290 | 4
281.2787 |  | 1125.1148 |  | 295 | 4
296.7596 |  | 1187.0386 |  | 300 | 4
318.8649 |  | 1275.4595 |  | 305 | 4
363.3945 |  | 1453.5781 |  | 310 | 4
444.1997 |  | 1776.7988 |  | 315 | 4
354.196 |  | 1416.7841 |  | 320 | 4
369.8017 |  | 1479.207 |  | 325 | 4
349.9448 |  | 1399.7792 |  | 330 | 4
420.3858 |  | 1681.5432 |  | 335 | 4
488.5667 |  | 1954.2666 |  | 340 | 4
521.9844 |  | 2087.9377 |  | 345 | 4
505.6253 |  | 2022.5013 |  | 350 | 4
574.3443 |  | 2297.3772 |  | 355 | 4
779.3703 |  | 3117.4812 |  | 360 | 4
828.3867 |  | 3313.5469 |  | 365 | 4
735.2985 |  | 2941.1939 |  | 370 | 4
849.7583 |  | 3399.0334 |  | 375 | 4
885.1134 |  | 3540.4535 |  | 380 | 4
853.0786 |  | 3412.3143 |  | 385 | 4
985.3832 |  | 3941.533 |  | 390 | 4
1109.0835 |  | 4436.3339 |  | 395 | 4
1226.3032 |  | 4905.2129 |  | 400 | 5
1350.8245 |  | 5403.298 |  | 450 | 5
247.4852 |  | 247.4852 |  | 500 | 5
163.5527 |  | 163.5527 |  | 550 | 5
183.5729 |  | 183.5729 |  | 600 | 5
281.2787 |  | 281.2787 |  | 650 | 6
296.7596 |  | 296.7596 |  | 700 | 6
318.8649 |  | 318.8649 |  | 750 | 6
363.3945 |  | 363.3945 |  | 800 | 6
444.1997 |  | 444.1997 |  | 850 | 6
354.196 |  | 354.196 |  | 900 | 6
369.8017 |  | 369.8017 |  | 950 | 8
349.9448 |  | 349.9448 |  | 1000 | 8
420.3858 |  | 420.3858 |  | 1050 | 8
488.5667 |  | 488.5667 |  | 1100 | 8
521.9844 |  | 521.9844 |  | 1150 | 8
505.6253 |  | 505.6253 |  | 1200 | 8
574.3443 |  | 574.3443 |  | 1250 | 8
779.3703 |  | 779.3703 |  | 1300 | 8
828.3867 |  | 828.3867 |  | 1350 | 8
735.2985 |  | 735.2985 |  | 1400 | 8
849.7583 |  | 849.7583 |  | 1450 | 8
885.1134 |  | 885.1134 |  | 1500 | 8
853.0786 |  | 853.0786 |  | 1550 | 8
985.3832 |  | 985.3832 |  | 1600 | 10
1109.0835 |  | 1109.0835 |  | 1650 | 10
1226.3032 |  | 1226.3032 |  | 1700 | 10
1350.8245 |  | 1350.8245 |  | 1750 | 10
247.4852 |  | 494.9704 |  | 1800 | 10
163.5527 |  | 327.1054 |  | 1850 | 10
183.5729 |  | 367.1458 |  | 1900 | 10
281.2787 |  | 562.5574 |  | 1950 | 10
296.7596 |  | 593.5193 |  | 2000 | 10
318.8649 |  | 637.7298 |  | 2050 | 10
363.3945 |  | 726.789 |  | 2100 | 10
444.1997 |  | 888.3994 |  | 2150 | 10
354.196 |  | 708.3921 |  | 2200 | 10
369.8017 |  | 739.6035 |  | 2250 | 10
349.9448 |  | 699.8896 |  | 2300 | 10
420.3858 |  | 840.7716 |  | 2350 | 10
488.5667 |  | 977.1333 |  | 2400 | 10
521.9844 |  | 1043.9688 |  | 2450 | 10
505.6253 |  | 1011.2506 |  | 2500 | 12
574.3443 |  | 1148.6886 |  | 2550 | 12
779.3703 |  | 1558.7406 |  | 2600 | 12
828.3867 |  | 1656.7734 |  | 2650 | 12
735.2985 |  | 1470.5969 |  | 2700 | 12
849.7583 |  | 1699.5167 |  | 2750 | 12
885.1134 |  | 1770.2267 |  | 2800 | 12
853.0786 |  | 1706.1572 |  | 2850 | 12
985.3832 |  | 1970.7665 |  | 2900 | 12
1109.0835 |  | 2218.1669 |  | 2950 | 12
1226.3032 |  | 2452.6065 |  | 3000 | 12
1350.8245 |  | 2701.649 |  | 3050 | 12
247.4852 |  | 742.4556 |  | 3100 | 12
163.5527 |  | 490.658 |  | 3150 | 12
183.5729 |  | 550.7188 |  | 3200 | 12
281.2787 |  | 843.8361 |  | 3250 | 12
296.7596 |  | 890.2789 |  | 3300 | 12
318.8649 |  | 956.5946 |  | 3350 | 12
363.3945 |  | 1090.1836 |  | 3400 | 12
444.1997 |  | 1332.5991 |  | 3450 | 12
354.196 |  | 1062.5881 |  | 3500 | 12
369.8017 |  | 1109.4052 |  | 3550 | 14
349.9448 |  | 1049.8344 |  | 3600 | 14
420.3858 |  | 1261.1574 |  | 3650 | 14
488.5667 |  | 1465.7 |  | 3700 | 14
521.9844 |  | 1565.9533 |  | 3750 | 14
505.6253 |  | 1516.876 |  | 3800 | 14
574.3443 |  | 1723.0329 |  | 3850 | 14
779.3703 |  | 2338.1109 |  | 3900 | 14
828.3867 |  | 2485.1601 |  | 3950 | 14
735.2985 |  | 2205.8954 |  | 4000 | 14
849.7583 |  | 2549.275 |  | 4050 | 14
885.1134 |  | 2655.3401 |  | 4100 | 14
853.0786 |  | 2559.2358 |  | 4150 | 14
985.3832 |  | 2956.1497 |  | 4200 | 14
1109.0835 |  | 3327.2504 |  | 4250 | 16
1226.3032 |  | 3678.9097 |  | 4300 | 16
1350.8245 |  | 4052.4735 |  | 4350 | 16
247.4852 |  | 989.9408 |  | 4400 | 16
163.5527 |  | 654.2107 |  | 4450 | 16
183.5729 |  | 734.2917 |  | 4500 | 16
281.2787 |  | 1125.1148 |  | 4550 | 16
296.7596 |  | 1187.0386 |  | 4600 | 16
318.8649 |  | 1275.4595 |  | 4650 | 16
363.3945 |  | 1453.5781 |  | 4700 | 16
444.1997 |  | 1776.7988 |  | 4750 | 16
354.196 |  | 1416.7841 |  | 4800 | 16
369.8017 |  | 1479.207 |  | 4850 | 16
349.9448 |  | 1399.7792 |  | 4900 | 16
420.3858 |  | 1681.5432 |  | 4950 | 16
488.5667 |  | 1954.2666 |  | 5000 | 16
521.9844 |  | 2087.9377 |  | 5050 | 16
505.6253 |  | 2022.5013 |  | 5100 | 16
574.3443 |  | 2297.3772 |  | 5150 | 16
779.3703 |  | 3117.4812 |  | 5200 | 16
828.3867 |  | 3313.5469 |  | 5250 | 16
735.2985 |  | 2941.1939 |  | 5300 | 16
849.7583 |  | 3399.0334 |  | 5350 | 16
885.1134 |  | 3540.4535 |  | 5400 | 16
853.0786 |  | 3412.3143 |  | 5450 | 16
985.3832 |  | 3941.533 |  | 5500 | 16
1109.0835 |  | 4436.3339 |  | 5550 | 18
1226.3032 |  | 4905.2129 |  | 5600 | 18
1350.8245 |  | 5403.298 |  | 5650 | 18
|  |  |  | 5700 | 18
|  |  |  | 5750 | 18
|  |  |  | 5800 | 18
|  |  |  | 5850 | 18
|  |  |  | 6000 | 18
|  |  |  | 6150 | 18
|  |  |  | 6300 | 18
|  |  |  | 6450 | 18
|  |  |  | 6600 | 18
|  |  |  | 6750 | 18
|  |  |  | 6900 | 18
|  |  |  | 7050 | 20
|  |  |  | 7200 | 20
|  |  |  | 7350 | 20
|  |  |  | 7500 | 20
|  |  |  | 7650 | 20
|  |  |  | 7800 | 20
|  |  |  | 7950 | 20
|  |  |  | 8100 | 20
|  |  |  | 8250 | 20
|  |  |  | 8400 | 20
|  |  |  | 8550 | 20
|  |  |  | 8700 | 20
|  |  |  | 8850 | 24
|  |  |  | 9000 | 24
|  |  |  | 9150 | 24
|  |  |  | 9300 | 24
|  |  |  | 9450 | 24
|  |  |  | 9600 | 24
|  |  |  | 9750 | 24
|  |  |  | 9900 | 24
|  |  |  | 10050 | 24
|  |  |  | 10200 | 24
|  |  |  | 10350 | 24
|  |  |  | 10500 | 24
|  |  |  | 10650 | 24
|  |  |  | 10800 | 24
|  |  |  | 10950 | 24
|  |  |  | 11100 | 24
|  |  |  | 11250 | 24
|  |  |  | 11400 | 24
|  |  |  | 11550 | 24
|  |  |  | 11700 | 24
|  |  |  | 11850 | 24
|  |  |  | 12000 | 24
|  |  |  | 12150 | 24
|  |  |  | 12300 | 24
|  |  |  | 12450 | 24
|  |  |  | 12600 | 24