## GES_VLS_CUE
Sequencing | Pump Size ID | Pump Size | Curve | Max flow @ max speed (gpm), 1 pump | Max Branch Flow | Max Header Flow | Number of Active Pumps | Number of Backup Pumps | Number of Total Pumps | Cost Group | Cost Group Type | Suction | Discharge | Branch Minimum | Branch Maximum | Header Minimum | Header Maximum
1 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 |  |  | 2 | 0 |  | A | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
2 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 |  |  | 2 | 0 |  | A | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
3 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 |  |  | 2 | 0 |  | A | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
4 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 |  |  | 2 | 0 |  | A | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
5 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 |  |  | 2 | 0 |  | A | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
6 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 |  |  | 2 | 0 |  | A | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
7 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 |  |  | 2 | 0 |  | A | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
8 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 |  |  | 2 | 0 |  | A | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
9 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 |  |  | 2 | 0 |  | A | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
10 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
11 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
12 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
13 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
14 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
15 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
16 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
17 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
18 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
19 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
20 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
21 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
22 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
23 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
24 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
25 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
26 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
27 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
28 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
29 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
30 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
31 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
32 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
33 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
34 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
35 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
36 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
37 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
38 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
39 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
40 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
41 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
42 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
43 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
44 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 |  |  | 2 | 0 |  | A | VLS_Inline | 2 | 2 | 2 |  | 2.5
45 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
46 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
47 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
48 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
49 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
50 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
51 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
52 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
53 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
54 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
55 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
56 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
57 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
58 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
59 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
60 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
61 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 |  |  | 2 | 0 |  | A | VLS_Inline | 2.5 | 2.5 |  |  | 3
62 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
63 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
64 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
65 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
66 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
67 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
68 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
69 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
70 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
71 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
72 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
73 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
74 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
75 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
76 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
77 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
78 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
79 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
80 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
81 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
82 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 |  |  | 2 | 0 |  | A | VLS_Inline | 3 | 3 |  |  | 4
83 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
84 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
85 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
86 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
87 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
88 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
89 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
90 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
91 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
92 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
93 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
94 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
95 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
96 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
97 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
98 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
99 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
100 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
101 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
102 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
103 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
104 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
105 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
106 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
107 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
108 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
109 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
110 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
111 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
112 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
113 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
114 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
115 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
116 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
117 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
118 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
119 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
120 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
121 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 |  |  | 2 | 0 |  | A | VLS_Inline | 4 | 4 |  |  | 5
122 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
123 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
124 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
125 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
126 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
127 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
128 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
129 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
130 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
131 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
132 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
133 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
134 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
135 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
136 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
137 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
138 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
139 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
140 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
141 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
142 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
143 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
144 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
145 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
146 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
147 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
148 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
149 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
150 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
151 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
152 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
153 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
154 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
155 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
156 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
157 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
158 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
159 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
160 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
161 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 |  |  | 2 | 0 |  | A | VLS_Inline | 5 | 5 |  |  | 6
162 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
163 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
164 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
165 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
166 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
167 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
168 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
169 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
170 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
171 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
172 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
173 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
174 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 |  |  | 2 | 0 |  | A | VLS_Inline | 6 | 6 |  |  | 8
175 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
176 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
177 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
178 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
179 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
180 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
181 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
182 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
183 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
184 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
185 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
186 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
187 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 |  |  | 2 | 0 |  | A | VLS_Inline | 8 | 8 |  |  | 10
188 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 |  |  | 2 | 0 |  | A | VLS_Inline | 10 | 10 |  |  | 12
189 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 |  |  | 2 | 0 |  | A | VLS_Inline | 10 | 10 |  |  | 12
190 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 |  |  | 2 | 0 |  | A | VLS_Inline | 10 | 10 |  |  | 12
191 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 |  | 3 | 0 |  | B | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
192 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 |  | 3 | 0 |  | B | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
193 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 |  | 3 | 0 |  | B | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
194 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 |  | 3 | 0 |  | B | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
195 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 |  | 3 | 0 |  | B | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
196 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 |  | 3 | 0 |  | B | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
197 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 |  | 3 | 0 |  | B | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
198 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 |  | 3 | 0 |  | B | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
199 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 |  | 3 | 0 |  | B | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
200 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
201 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
202 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
203 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
204 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
205 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
206 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
207 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
208 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
209 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
210 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
211 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
212 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
213 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
214 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
215 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
216 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
217 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
218 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
219 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
220 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
221 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
222 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
223 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
224 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
225 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
226 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
227 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
228 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
229 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
230 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
231 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
232 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
233 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
234 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 |  | 3 | 0 |  | B | VLS_Inline | 2 | 2 | 2 |  | 2.5
235 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
236 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
237 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
238 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
239 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
240 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
241 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
242 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
243 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
244 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
245 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
246 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
247 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
248 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
249 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
250 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
251 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 |  | 3 | 0 |  | B | VLS_Inline | 2.5 | 2.5 |  |  | 3
252 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
253 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
254 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
255 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
256 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
257 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
258 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
259 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
260 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
261 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
262 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
263 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
264 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
265 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
266 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
267 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
268 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
269 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
270 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
271 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
272 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 |  | 3 | 0 |  | B | VLS_Inline | 3 | 3 |  |  | 4
273 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
274 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
275 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
276 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
277 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
278 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
279 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
280 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
281 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
282 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
283 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
284 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
285 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
286 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
287 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
288 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
289 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
290 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
291 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
292 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
293 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
294 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
295 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
296 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
297 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
298 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
299 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
300 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
301 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
302 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
303 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
304 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
305 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
306 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
307 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
308 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
309 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
310 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
311 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 |  | 3 | 0 |  | B | VLS_Inline | 4 | 4 |  |  | 5
312 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
313 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
314 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
315 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
316 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
317 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
318 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
319 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
320 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
321 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
322 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
323 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
324 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
325 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
326 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
327 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
328 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
329 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
330 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
331 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
332 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
333 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
334 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
335 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
336 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
337 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
338 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
339 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
340 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
341 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
342 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
343 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
344 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
345 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
346 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
347 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
348 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
349 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
350 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
351 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 |  | 3 | 0 |  | B | VLS_Inline | 5 | 5 |  |  | 6
352 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
353 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
354 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
355 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
356 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
357 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
358 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
359 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
360 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
361 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
362 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
363 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
364 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 |  | 3 | 0 |  | B | VLS_Inline | 6 | 6 |  |  | 8
365 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
366 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
367 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
368 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
369 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
370 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
371 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
372 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
373 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
374 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
375 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
376 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
377 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 |  | 3 | 0 |  | B | VLS_Inline | 8 | 8 |  |  | 10
378 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 |  | 3 | 0 |  | B | VLS_Inline | 10 | 10 |  |  | 12
379 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 |  | 3 | 0 |  | B | VLS_Inline | 10 | 10 |  |  | 12
380 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 |  | 3 | 0 |  | B | VLS_Inline | 10 | 10 |  |  | 12
381 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 |  | 4 | 0 |  | C | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
382 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 |  | 4 | 0 |  | C | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
383 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 |  | 4 | 0 |  | C | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
384 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 |  | 4 | 0 |  | C | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
385 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 |  | 4 | 0 |  | C | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
386 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 |  | 4 | 0 |  | C | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
387 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 |  | 4 | 0 |  | C | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
388 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 |  | 4 | 0 |  | C | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
389 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 |  | 4 | 0 |  | C | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
390 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
391 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
392 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
393 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
394 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
395 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
396 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
397 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
398 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
399 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
400 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
401 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
402 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
403 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
404 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
405 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
406 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
407 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
408 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
409 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
410 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
411 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
412 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
413 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
414 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
415 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
416 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
417 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
418 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
419 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
420 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
421 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
422 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
423 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
424 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 |  | 4 | 0 |  | C | VLS_Inline | 2 | 2 | 2 |  | 2.5
425 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
426 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
427 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
428 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
429 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
430 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
431 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
432 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
433 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
434 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
435 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
436 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
437 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
438 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
439 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
440 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
441 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 |  | 4 | 0 |  | C | VLS_Inline | 2.5 | 2.5 |  |  | 3
442 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
443 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
444 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
445 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
446 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
447 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
448 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
449 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
450 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
451 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
452 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
453 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
454 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
455 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
456 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
457 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
458 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
459 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
460 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
461 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
462 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 |  | 4 | 0 |  | C | VLS_Inline | 3 | 3 |  |  | 4
463 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
464 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
465 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
466 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
467 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
468 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
469 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
470 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
471 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
472 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
473 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
474 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
475 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
476 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
477 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
478 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
479 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
480 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
481 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
482 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
483 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
484 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
485 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
486 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
487 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
488 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
489 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
490 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
491 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
492 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
493 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
494 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
495 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
496 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
497 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
498 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
499 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
500 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
501 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 |  | 4 | 0 |  | C | VLS_Inline | 4 | 4 |  |  | 5
502 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
503 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
504 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
505 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
506 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
507 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
508 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
509 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
510 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
511 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
512 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
513 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
514 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
515 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
516 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
517 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
518 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
519 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
520 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
521 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
522 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
523 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
524 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
525 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
526 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
527 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
528 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
529 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
530 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
531 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
532 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
533 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
534 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
535 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
536 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
537 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
538 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
539 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
540 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
541 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 |  | 4 | 0 |  | C | VLS_Inline | 5 | 5 |  |  | 6
542 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
543 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
544 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
545 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
546 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
547 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
548 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
549 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
550 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
551 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
552 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
553 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
554 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 |  | 4 | 0 |  | C | VLS_Inline | 6 | 6 |  |  | 8
555 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
556 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
557 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
558 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
559 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
560 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
561 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
562 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
563 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
564 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
565 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
566 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
567 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 |  | 4 | 0 |  | C | VLS_Inline | 8 | 8 |  |  | 10
568 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 |  | 4 | 0 |  | C | VLS_Inline | 10 | 10 |  |  | 12
569 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 |  | 4 | 0 |  | C | VLS_Inline | 10 | 10 |  |  | 12
570 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 |  | 4 | 0 |  | C | VLS_Inline | 10 | 10 |  |  | 12
571 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 |  | 1 | 1 |  | D | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
572 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 |  | 1 | 1 |  | D | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
573 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 |  | 1 | 1 |  | D | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
574 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 |  | 1 | 1 |  | D | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
575 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 |  | 1 | 1 |  | D | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
576 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 |  | 1 | 1 |  | D | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
577 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 |  | 1 | 1 |  | D | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
578 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 |  | 1 | 1 |  | D | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
579 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 |  | 1 | 1 |  | D | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
580 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
581 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
582 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
583 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
584 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
585 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
586 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
587 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
588 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
589 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
590 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
591 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
592 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
593 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
594 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
595 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
596 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
597 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
598 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
599 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
600 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
601 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
602 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
603 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
604 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
605 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
606 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
607 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
608 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
609 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
610 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
611 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
612 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
613 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
614 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 |  | 1 | 1 |  | D | VLS_Inline | 2 | 2 | 2 |  | 2.5
615 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
616 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
617 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
618 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
619 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
620 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
621 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
622 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
623 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
624 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
625 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
626 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
627 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
628 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
629 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
630 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
631 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 |  | 1 | 1 |  | D | VLS_Inline | 2.5 | 2.5 |  |  | 3
632 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
633 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
634 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
635 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
636 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
637 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
638 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
639 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
640 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
641 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
642 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
643 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
644 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
645 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
646 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
647 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
648 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
649 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
650 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
651 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
652 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 |  | 1 | 1 |  | D | VLS_Inline | 3 | 3 |  |  | 4
653 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
654 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
655 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
656 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
657 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
658 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
659 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
660 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
661 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
662 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
663 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
664 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
665 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
666 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
667 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
668 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
669 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
670 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
671 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
672 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
673 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
674 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
675 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
676 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
677 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
678 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
679 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
680 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
681 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
682 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
683 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
684 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
685 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
686 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
687 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
688 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
689 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
690 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
691 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 |  | 1 | 1 |  | D | VLS_Inline | 4 | 4 |  |  | 5
692 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
693 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
694 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
695 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
696 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
697 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
698 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
699 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
700 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
701 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
702 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
703 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
704 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
705 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
706 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
707 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
708 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
709 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
710 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
711 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
712 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
713 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
714 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
715 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
716 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
717 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
718 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
719 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
720 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
721 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
722 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
723 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
724 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
725 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
726 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
727 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
728 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
729 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
730 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
731 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 |  | 1 | 1 |  | D | VLS_Inline | 5 | 5 |  |  | 6
732 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
733 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
734 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
735 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
736 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
737 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
738 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
739 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
740 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
741 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
742 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
743 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
744 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 |  | 1 | 1 |  | D | VLS_Inline | 6 | 6 |  |  | 8
745 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
746 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
747 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
748 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
749 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
750 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
751 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
752 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
753 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
754 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
755 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
756 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
757 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 |  | 1 | 1 |  | D | VLS_Inline | 8 | 8 |  |  | 10
758 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 |  | 1 | 1 |  | D | VLS_Inline | 10 | 10 |  |  | 12
759 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 |  | 1 | 1 |  | D | VLS_Inline | 10 | 10 |  |  | 12
760 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 |  | 1 | 1 |  | D | VLS_Inline | 10 | 10 |  |  | 12
761 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 |  | 2 | 1 |  | E | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
762 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 |  | 2 | 1 |  | E | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
763 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 |  | 2 | 1 |  | E | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
764 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 |  | 2 | 1 |  | E | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
765 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 |  | 2 | 1 |  | E | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
766 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 |  | 2 | 1 |  | E | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
767 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 |  | 2 | 1 |  | E | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
768 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 |  | 2 | 1 |  | E | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
769 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 |  | 2 | 1 |  | E | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
770 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
771 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
772 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
773 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
774 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
775 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
776 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
777 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
778 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
779 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
780 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
781 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
782 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
783 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
784 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
785 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
786 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
787 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
788 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
789 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
790 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
791 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
792 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
793 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
794 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
795 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
796 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
797 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
798 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
799 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
800 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
801 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
802 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
803 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
804 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 |  | 2 | 1 |  | E | VLS_Inline | 2 | 2 | 2 |  | 2.5
805 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
806 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
807 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
808 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
809 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
810 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
811 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
812 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
813 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
814 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
815 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
816 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
817 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
818 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
819 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
820 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
821 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 |  | 2 | 1 |  | E | VLS_Inline | 2.5 | 2.5 |  |  | 3
822 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
823 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
824 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
825 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
826 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
827 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
828 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
829 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
830 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
831 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
832 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
833 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
834 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
835 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
836 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
837 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
838 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
839 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
840 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
841 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
842 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 |  | 2 | 1 |  | E | VLS_Inline | 3 | 3 |  |  | 4
843 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
844 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
845 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
846 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
847 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
848 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
849 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
850 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
851 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
852 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
853 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
854 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
855 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
856 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
857 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
858 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
859 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
860 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
861 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
862 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
863 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
864 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
865 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
866 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
867 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
868 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
869 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
870 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
871 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
872 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
873 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
874 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
875 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
876 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
877 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
878 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
879 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
880 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
881 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 |  | 2 | 1 |  | E | VLS_Inline | 4 | 4 |  |  | 5
882 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
883 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
884 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
885 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
886 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
887 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
888 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
889 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
890 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
891 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
892 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
893 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
894 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
895 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
896 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
897 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
898 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
899 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
900 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
901 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
902 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
903 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
904 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
905 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
906 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
907 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
908 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
909 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
910 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
911 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
912 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
913 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
914 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
915 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
916 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
917 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
918 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
919 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
920 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
921 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 |  | 2 | 1 |  | E | VLS_Inline | 5 | 5 |  |  | 6
922 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
923 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
924 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
925 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
926 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
927 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
928 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
929 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
930 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
931 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
932 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
933 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
934 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 |  | 2 | 1 |  | E | VLS_Inline | 6 | 6 |  |  | 8
935 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
936 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
937 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
938 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
939 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
940 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
941 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
942 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
943 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
944 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
945 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
946 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
947 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 |  | 2 | 1 |  | E | VLS_Inline | 8 | 8 |  |  | 10
948 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 |  | 2 | 1 |  | E | VLS_Inline | 10 | 10 |  |  | 12
949 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 |  | 2 | 1 |  | E | VLS_Inline | 10 | 10 |  |  | 12
950 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 |  | 2 | 1 |  | E | VLS_Inline | 10 | 10 |  |  | 12
951 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 |  | 3 | 1 |  | F | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
952 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 |  | 3 | 1 |  | F | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
953 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 |  | 3 | 1 |  | F | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
954 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 |  | 3 | 1 |  | F | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
955 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 |  | 3 | 1 |  | F | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
956 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 |  | 3 | 1 |  | F | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
957 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 |  | 3 | 1 |  | F | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
958 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 |  | 3 | 1 |  | F | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
959 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 |  | 3 | 1 |  | F | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
960 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
961 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
962 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
963 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
964 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
965 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
966 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
967 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
968 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
969 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
970 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
971 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
972 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
973 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
974 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
975 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
976 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
977 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
978 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
979 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
980 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
981 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
982 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
983 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
984 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
985 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
986 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
987 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
988 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
989 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
990 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
991 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
992 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
993 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
994 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 |  | 3 | 1 |  | F | VLS_Inline | 2 | 2 | 2 |  | 2.5
995 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
996 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
997 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
998 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
999 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1000 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1001 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1002 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1003 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1004 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1005 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1006 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1007 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1008 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1009 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1010 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1011 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 |  | 3 | 1 |  | F | VLS_Inline | 2.5 | 2.5 |  |  | 3
1012 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1013 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1014 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1015 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1016 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1017 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1018 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1019 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1020 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1021 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1022 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1023 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1024 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1025 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1026 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1027 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1028 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1029 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1030 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1031 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1032 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 |  | 3 | 1 |  | F | VLS_Inline | 3 | 3 |  |  | 4
1033 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1034 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1035 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1036 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1037 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1038 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1039 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1040 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1041 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1042 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1043 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1044 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1045 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1046 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1047 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1048 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1049 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1050 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1051 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1052 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1053 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1054 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1055 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1056 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1057 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1058 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1059 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1060 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1061 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1062 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1063 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1064 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1065 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1066 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1067 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1068 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1069 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1070 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1071 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 |  | 3 | 1 |  | F | VLS_Inline | 4 | 4 |  |  | 5
1072 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1073 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1074 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1075 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1076 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1077 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1078 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1079 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1080 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1081 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1082 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1083 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1084 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1085 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1086 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1087 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1088 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1089 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1090 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1091 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1092 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1093 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1094 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1095 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1096 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1097 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1098 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1099 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1100 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1101 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1102 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1103 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1104 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1105 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1106 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1107 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1108 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1109 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1110 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1111 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 |  | 3 | 1 |  | F | VLS_Inline | 5 | 5 |  |  | 6
1112 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1113 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1114 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1115 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1116 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1117 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1118 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1119 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1120 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1121 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1122 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1123 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1124 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 |  | 3 | 1 |  | F | VLS_Inline | 6 | 6 |  |  | 8
1125 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1126 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1127 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1128 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1129 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1130 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1131 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1132 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1133 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1134 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1135 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1136 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1137 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 |  | 3 | 1 |  | F | VLS_Inline | 8 | 8 |  |  | 10
1138 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 |  | 3 | 1 |  | F | VLS_Inline | 10 | 10 |  |  | 12
1139 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 |  | 3 | 1 |  | F | VLS_Inline | 10 | 10 |  |  | 12
1140 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 |  | 3 | 1 |  | F | VLS_Inline | 10 | 10 |  |  | 12
1141 | 1 | 12707-2P-5HP VLSC | VLSC_12707_2P_5HP | 120.9035 | 120.9035 | 241.807 | 4 | 1 |  | G | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
1142 | 2 | 12707-2P-7.5HP VLSC | VLSC_12707_2P_7.5HP | 134.1949 | 134.1949 | 268.3898 | 4 | 1 |  | G | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
1143 | 3 | 12707-2P-10HP VLSC | VLSC_12707_2P_10HP | 146.7341 | 146.7341 | 293.4682 | 4 | 1 |  | G | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
1144 | 4 | 12707-2P-15HP VLSC | VLSC_12707_2P_15HP | 154 | 154 | 308 | 4 | 1 |  | G | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
1145 | 5 | 12707-4P-3HP VLSC | VLSC_12707_4P_3HP | 79 | 79 | 158 | 4 | 1 |  | G | VLS_Inline | 1.25 | 1.25 | 2 |  | 2.5
1146 | 6 | 15709-2P-7.5HP VLSC | VLSC_15709_2P_7.5HP | 169.9715 | 169.9715 | 339.9431 | 4 | 1 |  | G | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
1147 | 7 | 15709-2P-10HP VLSC | VLSC_15709_2P_10HP | 191.939 | 191.939 | 383.8779 | 4 | 1 |  | G | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
1148 | 8 | 15709-2P-15HP VLSC | VLSC_15709_2P_15HP | 226.3257 | 226.3257 | 452.6514 | 4 | 1 |  | G | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
1149 | 9 | 15709-4P-3HP VLSC | VLSC_15709_4P_3HP | 124.0691 | 124.0691 | 248.1382 | 4 | 1 |  | G | VLS_Inline | 1.5 | 1.5 | 2 |  | 2.5
1150 | 10 | 20705-2P-7.5HP VLSC | VLSC_20705_2P_7.5HP | 190.191 | 190.191 | 380.3819 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1151 | 11 | 20705-2P-10HP VLSC | VLSC_20705_2P_10HP | 214.0515 | 214.0515 | 428.1031 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1152 | 12 | 20705-2P-15HP VLSC | VLSC_20705_2P_15HP | 249.8523 | 249.8523 | 499.7046 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1153 | 13 | 20705-2P-20HP VLSC | VLSC_20705_2P_20HP | 243.9916 | 243.9916 | 487.9832 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1154 | 14 | 20705-4P-3HP VLSC | VLSC_20705_4P_3HP | 128.156 | 128.156 | 256.3121 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1155 | 15 | 20951-2P-15HP VLSC | RC2511-7.70 | 152.95 | 152.95 | 305.9 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1156 | 16 | 20951-2P-20HP VLSC | RC2511-8.31 | 168.2305 | 168.2305 | 336.461 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1157 | 17 | 20951-2P-25HP VLSC | RC2511-8.84 | 184.528 | 184.528 | 369.056 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1158 | 18 | 20951-2P-30HP VLSC | RC2511-9.44 | 191.32 | 191.32 | 382.64 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1159 | 19 | 20951-4P-3HP VLSC | RC2511-8.70 | 90.3291 | 90.3291 | 180.6582 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1160 | 20 | 20951-4P-5HP VLSC | RC2511-9.6 | 95.22 | 95.22 | 190.44 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1161 | 21 | 2095A-2P-15HP VLSC | VLSC_2095A_2P_15HP | 176.1225 | 176.1225 | 352.2451 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1162 | 22 | 2095A-2P-20HP VLSC | VLSC_2095A_2P_20HP | 200.368 | 200.368 | 400.7361 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1163 | 23 | 2095A-2P-25HP VLSC | VLSC_2095A_2P_25HP | 232.5586 | 232.5586 | 465.1173 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1164 | 24 | 2095A-2P-30HP VLSC | VLSC_2095A_2P_30HP | 232.5586 | 232.5586 | 465.1173 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1165 | 25 | 2095A-4P-3HP VLSC | VLSC_2095A_4P_3HP | 111.4482 | 111.4482 | 222.8964 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1166 | 26 | 2095A-4P-5HP VLSC | VLSC_2095A_4P_5HP | 118.6369 | 118.6369 | 237.2737 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1167 | 27 | 20955-2P-15HP VLSC | VLSC_20955_2P_15HP | 205.3636 | 205.3636 | 410.7272 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1168 | 28 | 20955-2P-20HP VLSC | VLSC_20955_2P_20HP | 235.6474 | 235.6474 | 471.2947 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1169 | 29 | 20955-2P-25HP VLSC | VLSC_20955_2P_25HP | 257.4 | 257.4 | 514.8 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1170 | 30 | 20955-2P-30HP VLSC | VLSC_20955_2P_30HP | 277.4627 | 277.4627 | 554.9253 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1171 | 31 | 20955-2P-40HP VLSC | VLSC_20955_2P_40HP | 300 | 300 | 600 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1172 | 32 | 20955-2P-50HP VLSC | VLSC_20955_2P_50HP | 300 | 300 | 600 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1173 | 33 | 20955-4P-3HP VLSC | VLSC_20955_4P_3HP | 136.1059 | 136.1059 | 272.2118 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1174 | 34 | 20955-4P-5HP VLSC | VLSC_20955_4P_5HP | 162.637 | 162.637 | 325.274 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1175 | 35 | 20955-4P-7.5HP VLSC | VLSC_20955_4P_7.5HP | 165.3271 | 165.3271 | 330.6542 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1176 | 36 | 20959-2P-20HP VLSC | VLSC_20959_2P_20HP | 271.9533 | 271.9533 | 543.9066 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1177 | 37 | 20959-2P-25HP VLSC | VLSC_20959_2P_25HP | 309.3395 | 309.3395 | 618.679 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1178 | 38 | 20959-2P-30HP VLSC | VLSC_20959_2P_30HP | 341.2848 | 341.2848 | 682.5695 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1179 | 39 | 20959-2P-40HP VLSC | VLSC_20959_2P_40HP | 380.858 | 380.858 | 761.716 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1180 | 40 | 20959-2P-50HP VLSC | VLSC_20959_2P_50HP | 405.1149 | 405.1149 | 810.2297 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1181 | 41 | 20959-2P-60HP VLSC | VLSC_20959_2P_60HP | 406.8778 | 406.8778 | 813.7556 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1182 | 42 | 20959-4P-3HP VLSC | VLSC_20959_4P_3HP | 154.2292 | 154.2292 | 308.4583 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1183 | 43 | 20959-4P-5HP VLSC | VLSC_20959_4P_5HP | 205.8649 | 205.8649 | 411.7298 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1184 | 44 | 20959-4P-7.5HP VLSC | VLSC_20959_4P_7.5HP | 227.7916 | 227.7916 | 455.5833 | 4 | 1 |  | G | VLS_Inline | 2 | 2 | 2 |  | 2.5
1185 | 45 | 25709-2P-10HP VLSC | VLSC_25709_2P_10HP | 294.5625 | 294.5625 | 589.1251 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1186 | 46 | 25709-2P-15HP VLSC | VLSC_25709_2P_15HP | 355.8818 | 355.8818 | 711.7636 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1187 | 47 | 25709-2P-20HP VLSC | VLSC_25709_2P_20HP | 415.2757 | 415.2757 | 830.5515 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1188 | 48 | 25709-2P-25HP VLSC | VLSC_25709_2P_25HP | 449.14 | 449.14 | 898.2801 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1189 | 49 | 25709-4P-3HP VLSC | VLSC_25709_4P_3HP | 222.9265 | 222.9265 | 445.8531 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1190 | 50 | 25953-2P-20HP VLSC | VLSC_25953_2P_20HP | 339.6329 | 339.6329 | 679.2659 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1191 | 51 | 25953-2P-25HP VLSC | VLSC_25953_2P_25HP | 384.0902 | 384.0902 | 768.1804 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1192 | 52 | 25953-2P-30HP VLSC | VLSC_25953_2P_30HP | 424.5536 | 424.5536 | 849.1072 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1193 | 53 | 25953-2P-40HP VLSC | VLSC_25953_2P_40HP | 491.3603 | 491.3603 | 982.7205 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1194 | 54 | 25953-2P-50HP VLSC | VLSC_25953_2P_50HP | 551.7418 | 551.7418 | 1103.4836 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1195 | 55 | 25953-2P-60HP VLSC | VLSC_25953_2P_60HP | 573.0512 | 573.0512 | 1146.1024 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1196 | 56 | 25953-4P-3HP VLSC | VLSC_25953_4P_3HP | 179.981 | 179.981 | 359.9621 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1197 | 57 | 25953-4P-5HP VLSC | VLSC_25953_4P_5HP | 237.9031 | 237.9031 | 475.8063 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1198 | 58 | 25953-4P-7.5HP VLSC | VLSC_25953_4P_7.5HP | 284.3868 | 284.3868 | 568.7735 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1199 | 59 | 25121-4P-7.5HP VLSC | VLSC_25121_4P_7.5HP | 260.585 | 260.585 | 521.17 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1200 | 60 | 25121-4P-10HP VLSC | VLSC_25121_4P_10HP | 273.2839 | 273.2839 | 546.5679 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1201 | 61 | 25121-4P-15HP VLSC | VLSC_25121_4P_15HP | 330.9972 | 330.9972 | 661.9944 | 4 | 1 |  | G | VLS_Inline | 2.5 | 2.5 |  |  | 3
1202 | 62 | 30707-2P-15HP VLSC | VLSC_30707_2P_15HP | 524.7552 | 524.7552 | 1049.5105 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1203 | 63 | 30707-2P-20HP VLSC | VLSC_30707_2P_20HP | 534.9404 | 534.9404 | 1069.8809 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1204 | 64 | 30707-2P-25HP VLSC | VLSC_30707_2P_25HP | 573.9449 | 573.9449 | 1147.8898 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1205 | 65 | 30707-2P-30HP VLSC | VLSC_30707_2P_30HP | 599.7227 | 599.7227 | 1199.4453 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1206 | 66 | 30957-2P-30HP VLSC | VLSC_30957_2P_30HP | 512.3923 | 512.3923 | 1024.7846 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1207 | 67 | 30957-2P-40HP VLSC | VLSC_30957_2P_40HP | 573.8168 | 573.8168 | 1147.6336 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1208 | 68 | 30957-2P-50HP VLSC | VLSC_30957_2P_50HP | 630.1667 | 630.1667 | 1260.3334 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1209 | 69 | 30957-2P-60HP VLSC | VLSC_30957_2P_60HP | 681.695 | 681.695 | 1363.39 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1210 | 70 | 30707-4P-3HP VLSC | VLSC_30707_4P_3HP | 242.0702 | 242.0702 | 484.1403 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1211 | 71 | 30707-4P-5HP VLSC | VLSC_30707_4P_5HP | 291.6367 | 291.6367 | 583.2733 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1212 | 72 | 30957-4P-5HP VLSC | VLSC_30957_4P_5HP | 290.4936 | 290.4936 | 580.9873 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1213 | 73 | 30957-4P-7.5HP VLSC | VLSC_30957_4P_7.5HP | 350.6693 | 350.6693 | 701.3387 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1214 | 74 | 30957-4P-10HP VLSC | VLSC_30957_4P_10HP | 375.4803 | 375.4803 | 750.9605 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1215 | 75 | 30123-4P-7.5HP VLSC | RC2539-9.07 | 402.5638 | 402.5638 | 805.1276 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1216 | 76 | 30123-4P-10HP VLSC | RC2539-9.91 | 427.3855 | 427.3855 | 854.771 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1217 | 77 | 30123-4P-15HP VLSC | RC2539-11.12 | 430.0891 | 430.0891 | 860.1783 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1218 | 78 | 30123-4P-20HP VLSC | RC2539-12.1 | 453.84 | 453.84 | 907.68 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1219 | 79 | 30125-4P-7.5HP VLSC | VLSC_30125_4P_7.5HP | 360.7205 | 360.7205 | 721.4409 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1220 | 80 | 30125-4P-10HP VLSC | VLSC_30125_4P_10HP | 391.3696 | 391.3696 | 782.7393 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1221 | 81 | 30125-4P-15HP VLSC | VLSC_30125_4P_15HP | 444.5377 | 444.5377 | 889.0754 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1222 | 82 | 30125-4P-20HP VLSC | VLSC_30125_4P_20HP | 455.5928 | 455.5928 | 911.1855 | 4 | 1 |  | G | VLS_Inline | 3 | 3 |  |  | 4
1223 | 83 | 40707-2P-15HP VLSC | VLSC_40707_2P_15HP | 548.8465 | 548.8465 | 1097.6931 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1224 | 84 | 40707-2P-20HP VLSC | VLSC_40707_2P_20HP | 628.8755 | 628.8755 | 1257.751 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1225 | 85 | 40707-2P-25HP VLSC | VLSC_40707_2P_25HP | 683.4996 | 683.4996 | 1366.9992 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1226 | 86 | 40707-2P-30HP VLSC | VLSC_40707_2P_30HP | 734.2064 | 734.2064 | 1468.4128 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1227 | 87 | 40707-2P-40HP VLSC | VLSC_40707_2P_40HP | 789.7994 | 789.7994 | 1579.5988 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1228 | 88 | 40707-4P-3HP VLSC | VLSC_40707_4P_3HP | 360.84 | 360.84 | 721.68 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1229 | 89 | 40707-4P-5HP VLSC | VLSC_40707_4P_5HP | 106.8596 | 106.8596 | 213.7192 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1230 | 90 | 40957-2P-40HP VLSC | RC9914-1-6.92-2P | 913.8143 | 913.8143 | 1827.6287 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1231 | 91 | 40957-2P-50HP VLSC | RC9914-1-7.60-2P | 969.4037 | 969.4037 | 1938.8074 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1232 | 92 | 40957-2P-60HP VLSC | RC9914-1-8.04-2P | 1015.343 | 1015.343 | 2030.6859 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1233 | 93 | 40957-2P-75HP VLSC | RC9914-1-8.58-2P | 1051.8577 | 1051.8577 | 2103.7154 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1234 | 94 | 40957-2P-100HP VLSC | RC9914-1-9.43-2P | 1127.0937 | 1127.0937 | 2254.1875 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1235 | 95 | 40957-4P-5HP VLSC | RC9914-1-6.91 | 456.5775 | 456.5775 | 913.1549 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1236 | 96 | 40957-4P-7.5HP VLSC | RC9914-1-8.04 | 508.0798 | 508.0798 | 1016.1596 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1237 | 97 | 40957-4P-10HP VLSC | RC9914-1-8.77 | 534.9443 | 534.9443 | 1069.8887 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1238 | 98 | 40957-4P-15HP VLSC | RC9914-1-9.6 | 568.82 | 568.82 | 1137.64 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1239 | 99 | 40959-2P-40HP VLSC | VLSC_40959_2P_40HP | 885.0742 | 885.0742 | 1770.1484 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1240 | 100 | 40959-2P-50HP VLSC | VLSC_40959_2P_50HP | 912.6252 | 912.6252 | 1825.2504 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1241 | 101 | 40959-2P-60HP VLSC | VLSC_40959_2P_60HP | 955.0129 | 955.0129 | 1910.0257 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1242 | 102 | 40959-2P-75HP VLSC | VLSC_40959_2P_75HP | 1024.8269 | 1024.8269 | 2049.6538 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1243 | 103 | 40959-2P-100HP VLSC | VLSC_40959_2P_100HP | 1116.5838 | 1116.5838 | 2233.1676 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1244 | 104 | 40959-4P-5HP VLSC | VLSC_40959_4P_5HP | 466.2681 | 466.2681 | 932.5363 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1245 | 105 | 40959-4P-7.5HP VLSC | VLSC_40959_4P_7.5HP | 509.7501 | 509.7501 | 1019.5003 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1246 | 106 | 40959-4P-10HP VLSC | VLSC_40959_4P_10HP | 543.4703 | 543.4703 | 1086.9406 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1247 | 107 | 40959-4P-15HP VLSC | VLSC_40959_4P_15HP | 607.7455 | 607.7455 | 1215.4911 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1248 | 108 | 40127-4P-15HP VLSC | RC9904-3-9.87 | 667.9 | 667.9 | 1335.8 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1249 | 109 | 40127-4P-20HP VLSC | RC9904-3-10.75 | 732.8 | 732.8 | 1465.6 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1250 | 110 | 40127-4P-25HP VLSC | RC9904-3-11.39 | 774.6 | 774.6 | 1549.2 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1251 | 111 | 40127-4P-30HP VLSC | RC9904-3-12.10-4P | 813.5 | 813.5 | 1627 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1252 | 112 | 40129-4P-15HP VLSC | VLSC_40129_4P_15HP | 616.3385 | 616.3385 | 1232.6769 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1253 | 113 | 40129-4P-20HP VLSC | VLSC_40129_4P_20HP | 707.5905 | 707.5905 | 1415.1811 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1254 | 114 | 40129-4P-25HP VLSC | VLSC_40129_4P_25HP | 786.8099 | 786.8099 | 1573.6198 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1255 | 115 | 40129-4P-30HP VLSC | VLSC_40129_4P_30HP | 825.5 | 825.5 | 1651 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1256 | 116 | 40157-4P-30HP VLSC | RC9947-1-12.0-4P | 756.8 | 756.8 | 1513.6 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1257 | 117 | 40157-4P-40HP VLSC | RC9947-1-13.41-4P | 830.5 | 830.5 | 1661 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1258 | 118 | 40157-4P-50HP VLSC | RC9947-1-14.10-4P | 873.3 | 873.3 | 1746.6 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1259 | 119 | 40159-4P-30HP VLSC | VLSC_40159_4P_30HP | 639.1572 | 639.1572 | 1278.3144 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1260 | 120 | 40159-4P-40HP VLSC | VLSC_40159_4P_40HP | 794.9133 | 794.9133 | 1589.8266 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1261 | 121 | 40159-4P-50HP VLSC | VLSC_40159_4P_50HP | 882.342 | 882.342 | 1764.6841 | 4 | 1 |  | G | VLS_Inline | 4 | 4 |  |  | 5
1262 | 122 | 50707-2P-30HP VLSC | VLSC_50707_2P_30HP | 935.9263 | 935.9263 | 1871.8526 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1263 | 123 | 50707-2P-40HP VLSC | VLSC_50707_2P_40HP | 1136.2741 | 1136.2741 | 2272.5482 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1264 | 124 | 50707-2P-50HP VLSC | VLSC_50707_2P_50HP | 1332.9681 | 1332.9681 | 2665.9362 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1265 | 125 | 50707-2P-60HP VLSC | VLSC_50707_2P_60HP | 1528.3535 | 1528.3535 | 3056.707 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1266 | 126 | 50707-4P-5HP VLSC | VLSC_50707_4P_5HP | 626.346 | 626.346 | 1252.6919 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1267 | 127 | 50707-4P-7.5HP VLSC | VLSC_50707_4P_7.5HP | 764.9699 | 764.9699 | 1529.9399 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1268 | 128 | 50957-4P-7.5HP VLSC | RC2552-7.24 | 682.0481 | 682.0481 | 1364.0961 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1269 | 129 | 50957-4P-10HP VLSC | RC2552-8.02 | 802.7921 | 802.7921 | 1605.5841 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1270 | 130 | 50957-4P-15HP VLSC | RC2552-9.10 | 932.9167 | 932.9167 | 1865.8335 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1271 | 131 | 50957-4P-20HP VLSC | RC2552-9.6 | 1000.0001 | 1000.0001 | 2000.0002 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1272 | 132 | 5095A-4P-7.5HP VLSC | VLSC_5095A_4P_7.5HP | 753.2463 | 753.2463 | 1506.4926 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1273 | 133 | 5095A-4P-10HP VLSC | VLSC_5095A_4P_10HP | 820.4429 | 820.4429 | 1640.8858 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1274 | 134 | 5095A-4P-15HP VLSC | VLSC_5095A_4P_15HP | 953.3171 | 953.3171 | 1906.6342 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1275 | 135 | 5095A-4P-20HP VLSC | VLSC_5095A_4P_20HP | 1029.7585 | 1029.7585 | 2059.5169 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1276 | 136 | 50959-2P-60HP VLSC | VLSC_50959_2P_60HP | 1330.3437 | 1330.3437 | 2660.6874 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1277 | 137 | 50959-2P-75HP VLSC | VLSC_50959_2P_75HP | 1378.5213 | 1378.5213 | 2757.0426 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1278 | 138 | 50959-2P-100HP VLSC | VLSC_50959_2P_100HP | 1467.9509 | 1467.9509 | 2935.9018 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1279 | 139 | 50129-4P-15HP VLSC | VLSC_50129_4P_15HP | 844.864 | 844.864 | 1689.7279 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1280 | 140 | 50129-4P-20HP VLSC | VLSC_50129_4P_20HP | 982.3526 | 982.3526 | 1964.7052 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1281 | 141 | 50129-4P-25HP VLSC | VLSC_50129_4P_25HP | 1104.8611 | 1104.8611 | 2209.7222 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1282 | 142 | 50129-4P-30HP VLSC | VLSC_50129_4P_30HP | 1214.4257 | 1214.4257 | 2428.8514 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1283 | 143 | 50129-4P-40HP VLSC | VLSC_50129_4P_40HP | 1383.6857 | 1383.6857 | 2767.3715 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1284 | 144 | 50129-4P-50HP VLSC | VLSC_50129_4P_50HP | 1551.2098 | 1551.2098 | 3102.4196 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1285 | 145 | 50129-4P-60HP VLSC | VLSC_50129_4P_60HP | 1664.6746 | 1664.6746 | 3329.3491 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1286 | 146 | 5012A-4P-10HP VLSC | RC9940-8.37 | 840.7876 | 840.7876 | 1681.5751 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1287 | 147 | 5012A-4P-15HP VLSC | RC9940-9.62 | 995.4751 | 995.4751 | 1990.9502 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1288 | 148 | 5012A-4P-20HP VLSC | RC9940-10.48 | 1093.6698 | 1093.6698 | 2187.3397 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1289 | 149 | 5012A-4P-25HP VLSC | RC9940-11.02 | 1144.8546 | 1144.8546 | 2289.7092 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1290 | 150 | 5012A-4P-30HP VLSC | RC9940-11.62-4P | 1204.5001 | 1204.5001 | 2409.0002 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1291 | 151 | 5012A-4P-40HP VLSC | RC9940-12.1-4P | 1252.5 | 1252.5 | 2505 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1292 | 152 | 5012C-4P-10HP VLSC | VLSC_5012C_4P_10HP | 648.3835 | 648.3835 | 1296.767 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1293 | 153 | 5012C-4P-15HP VLSC | VLSC_5012C_4P_15HP | 820.3589 | 820.3589 | 1640.7178 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1294 | 154 | 5012C-4P-20HP VLSC | VLSC_5012C_4P_20HP | 941.0352 | 941.0352 | 1882.0704 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1295 | 155 | 5012C-4P-25HP VLSC | VLSC_5012C_4P_25HP | 1045.3157 | 1045.3157 | 2090.6314 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1296 | 156 | 5012C-4P-30HP VLSC | VLSC_5012C_4P_30HP | 1136.5096 | 1136.5096 | 2273.0192 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1297 | 157 | 5012C-4P-40HP VLSC | VLSC_5012C_4P_40HP | 1235.933 | 1235.933 | 2471.866 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1298 | 158 | 50157-4P-50HP VLSC | VLSC_50157_4P_50HP | 1229.0007 | 1229.0007 | 2458.0014 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1299 | 159 | 50157-4P-60HP VLSC | VLSC_50157_4P_60HP | 1303.9328 | 1303.9328 | 2607.8655 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1300 | 160 | 50157-4P-75HP VLSC | VLSC_50157_4P_75HP | 1403.874 | 1403.874 | 2807.748 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1301 | 161 | 50157-4P-100HP VLSC | VLSC_50157_4P_100HP | 1484.3188 | 1484.3188 | 2968.6376 | 4 | 1 |  | G | VLS_Inline | 5 | 5 |  |  | 6
1302 | 162 | 60957-4P-15HP VLSC | VLSC_60957_4P_15HP | 1171.9065 | 1171.9065 | 2343.8131 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1303 | 163 | 60957-4P-20HP VLSC | VLSC_60957_4P_20HP | 1316.9347 | 1316.9347 | 2633.8694 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1304 | 164 | 60957-4P-25HP VLSC | VLSC_60957_4P_25HP | 1454.2378 | 1454.2378 | 2908.4756 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1305 | 165 | 60957-4P-30HP VLSC | VLSC_60957_4P_30HP | 1568.7217 | 1568.7217 | 3137.4434 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1306 | 166 | 60125-4P-20HP VLSC | VLSC_60125_4P_20HP | 1414.8836 | 1414.8836 | 2829.7672 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1307 | 167 | 60125-4P-25HP VLSC | VLSC_60125_4P_25HP | 1523.3743 | 1523.3743 | 3046.7486 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1308 | 168 | 60125-4P-30HP VLSC | VLSC_60125_4P_30HP | 1625.1171 | 1625.1171 | 3250.2342 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1309 | 169 | 60125-4P-40HP VLSC | VLSC_60125_4P_40HP | 1757.2796 | 1757.2796 | 3514.5593 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1310 | 170 | 60125-4P-50HP VLSC | VLSC_60125_4P_50HP | 1846.8509 | 1846.8509 | 3693.7017 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1311 | 171 | 60125-4P-60HP VLSC | VLSC_60125_4P_60HP | 1914.581 | 1914.581 | 3829.162 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1312 | 172 | 60157-4P-75HP VLSC | VLSC_60157_4P_75HP | 1634.3829 | 1634.3829 | 3268.7658 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1313 | 173 | 60157-4P-100HP VLSC | VLSC_60157_4P_100HP | 1915.2738 | 1915.2738 | 3830.5476 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1314 | 174 | 60157-4P-125HP VLSC | VLSC_60157_4P_125HP | 2165.2718 | 2165.2718 | 4330.5437 | 4 | 1 |  | G | VLS_Inline | 6 | 6 |  |  | 8
1315 | 175 | 80951-4P-20HP VLSC | VLSC_80951_4P_20HP | 1914.1469 | 1914.1469 | 3828.2938 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1316 | 176 | 80951-4P-25HP VLSC | VLSC_80951_4P_25HP | 2017.9874 | 2017.9874 | 4035.9748 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1317 | 177 | 80951-4P-30HP VLSC | VLSC_80951_4P_30HP | 2141.5995 | 2141.5995 | 4283.199 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1318 | 178 | 80951-4P-40HP VLSC | VLSC_80951_4P_40HP | 2290.5785 | 2290.5785 | 4581.157 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1319 | 179 | 80123-4P-25HP VLSC | VLSC_80123_4P_25HP | 1727.4951 | 1727.4951 | 3454.9903 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1320 | 180 | 80123-4P-30HP VLSC | VLSC_80123_4P_30HP | 1826.6982 | 1826.6982 | 3653.3965 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1321 | 181 | 80123-4P-40HP VLSC | VLSC_80123_4P_40HP | 2003.3556 | 2003.3556 | 4006.7112 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1322 | 182 | 80123-4P-50HP VLSC | VLSC_80123_4P_50HP | 2187.1986 | 2187.1986 | 4374.3972 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1323 | 183 | 80123-4P-60HP VLSC | VLSC_80123_4P_60HP | 2293.6739 | 2293.6739 | 4587.3477 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1324 | 184 | 80123-4P-75HP VLSC | VLSC_80123_4P_75HP | 2422.2984 | 2422.2984 | 4844.5968 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1325 | 185 | 80123-4P-100HP VLSC | VLSC_80123_4P_100HP | 2547.3614 | 2547.3614 | 5094.7228 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1326 | 186 | 80157-4P-100HP VLSC | VLSC_80157_4P_100HP | 2953.0528 | 2953.0528 | 5906.1056 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1327 | 187 | 80157-4P-125HP VLSC | VLSC_80157_4P_125HP | 3220.9607 | 3220.9607 | 6441.9215 | 4 | 1 |  | G | VLS_Inline | 8 | 8 |  |  | 10
1328 | 188 | 10123-4P-75HP VLSC | VLSC_10123_4P_75HP | 3579.8797 | 3579.8797 | 7159.7593 | 4 | 1 |  | G | VLS_Inline | 10 | 10 |  |  | 12
1329 | 189 | 10123-4P-100HP VLSC | VLSC_10123_4P_100HP | 3926.8748 | 3926.8748 | 7853.7497 | 4 | 1 |  | G | VLS_Inline | 10 | 10 |  |  | 12
1330 | 190 | 10123-4P-125HP VLSC | VLSC_10123_4P_125HP | 4128.2784 | 4128.2784 | 8256.5567 | 4 | 1 |  | G | VLS_Inline | 10 | 10 |  |  | 12

## Branch to Header min
Branch Minimum
2 | 2.5
2.5 | 3
3 | 4
4 | 5
5 | 6
6 | 8
8 | 10
10 | 12

## Max flow to diameter
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.) | Flow (gpm) | Pipe Diameter (in.)
120.9035 | 2.5 | 241.807 | 4 | 20 | 2
134.1949 | 3 | 268.3898 | 4 | 25 | 2
146.7341 |  | 293.4682 |  | 30 | 2
154 |  | 308 |  | 35 | 2
79 |  | 158 |  | 40 | 2
169.9715 |  | 339.9431 |  | 45 | 2
191.939 |  | 383.8779 |  | 50 | 2
226.3257 |  | 452.6514 |  | 55 | 2
124.0691 |  | 248.1382 |  | 60 | 2
190.191 |  | 380.3819 |  | 65 | 2
214.0515 |  | 428.1031 |  | 70 | 2
249.8523 |  | 499.7046 |  | 75 | 2
243.9916 |  | 487.9832 |  | 80 | 2
128.156 |  | 256.3121 |  | 85 | 2.5
152.95 |  | 305.9 |  | 90 | 2.5
168.2305 |  | 336.461 |  | 95 | 2.5
184.528 |  | 369.056 |  | 100 | 2.5
191.32 |  | 382.64 |  | 105 | 2.5
90.3291 |  | 180.6582 |  | 110 | 2.5
95.22 |  | 190.44 |  | 115 | 2.5
176.1225 |  | 352.2451 |  | 120 | 2.5
200.368 |  | 400.7361 |  | 125 | 3
232.5586 |  | 465.1173 |  | 130 | 3
232.5586 |  | 465.1173 |  | 135 | 3
111.4482 |  | 222.8964 |  | 140 | 3
118.6369 |  | 237.2737 |  | 145 | 3
205.3636 |  | 410.7272 |  | 150 | 3
235.6474 |  | 471.2947 |  | 155 | 3
257.4 |  | 514.8 |  | 160 | 3
277.4627 |  | 554.9253 |  | 165 | 3
300 |  | 600 |  | 170 | 3
300 |  | 600 |  | 175 | 3
136.1059 |  | 272.2118 |  | 180 | 3
162.637 |  | 325.274 |  | 185 | 3
165.3271 |  | 330.6542 |  | 190 | 3
271.9533 |  | 543.9066 |  | 195 | 3
309.3395 |  | 618.679 |  | 200 | 3
341.2848 |  | 682.5695 |  | 205 | 3
380.858 |  | 761.716 |  | 210 | 3
405.1149 |  | 810.2297 |  | 215 | 4
406.8778 |  | 813.7556 |  | 220 | 4
154.2292 |  | 308.4583 |  | 225 | 4
205.8649 |  | 411.7298 |  | 230 | 4
227.7916 |  | 455.5833 |  | 235 | 4
294.5625 |  | 589.1251 |  | 240 | 4
355.8818 |  | 711.7636 |  | 245 | 4
415.2757 |  | 830.5515 |  | 250 | 4
449.14 |  | 898.2801 |  | 255 | 4
222.9265 |  | 445.8531 |  | 260 | 4
339.6329 |  | 679.2659 |  | 265 | 4
384.0902 |  | 768.1804 |  | 270 | 4
424.5536 |  | 849.1072 |  | 275 | 4
491.3603 |  | 982.7205 |  | 280 | 4
551.7418 |  | 1103.4836 |  | 285 | 4
573.0512 |  | 1146.1024 |  | 290 | 4
179.981 |  | 359.9621 |  | 295 | 4
237.9031 |  | 475.8063 |  | 300 | 4
284.3868 |  | 568.7735 |  | 305 | 4
260.585 |  | 521.17 |  | 310 | 4
273.2839 |  | 546.5679 |  | 315 | 4
330.9972 |  | 661.9944 |  | 320 | 4
524.7552 |  | 1049.5105 |  | 325 | 4
534.9404 |  | 1069.8809 |  | 330 | 4
573.9449 |  | 1147.8898 |  | 335 | 4
599.7227 |  | 1199.4453 |  | 340 | 4
512.3923 |  | 1024.7846 |  | 345 | 4
573.8168 |  | 1147.6336 |  | 350 | 4
630.1667 |  | 1260.3334 |  | 355 | 4
681.695 |  | 1363.39 |  | 360 | 4
242.0702 |  | 484.1403 |  | 365 | 4
291.6367 |  | 583.2733 |  | 370 | 4
290.4936 |  | 580.9873 |  | 375 | 4
350.6693 |  | 701.3387 |  | 380 | 4
375.4803 |  | 750.9605 |  | 385 | 4
402.5638 |  | 805.1276 |  | 390 | 4
427.3855 |  | 854.771 |  | 395 | 4
430.0891 |  | 860.1783 |  | 400 | 5
453.84 |  | 907.68 |  | 450 | 5
360.7205 |  | 721.4409 |  | 500 | 5
391.3696 |  | 782.7393 |  | 550 | 5
444.5377 |  | 889.0754 |  | 600 | 5
455.5928 |  | 911.1855 |  | 650 | 6
548.8465 |  | 1097.6931 |  | 700 | 6
628.8755 |  | 1257.751 |  | 750 | 6
683.4996 |  | 1366.9992 |  | 800 | 6
734.2064 |  | 1468.4128 |  | 850 | 6
789.7994 |  | 1579.5988 |  | 900 | 6
360.84 |  | 721.68 |  | 950 | 8
106.8596 |  | 213.7192 |  | 1000 | 8
913.8143 |  | 1827.6287 |  | 1050 | 8
969.4037 |  | 1938.8074 |  | 1100 | 8
1015.343 |  | 2030.6859 |  | 1150 | 8
1051.8577 |  | 2103.7154 |  | 1200 | 8
1127.0937 |  | 2254.1875 |  | 1250 | 8
456.5775 |  | 913.1549 |  | 1300 | 8
508.0798 |  | 1016.1596 |  | 1350 | 8
534.9443 |  | 1069.8887 |  | 1400 | 8
568.82 |  | 1137.64 |  | 1450 | 8
885.0742 |  | 1770.1484 |  | 1500 | 8
912.6252 |  | 1825.2504 |  | 1550 | 8
955.0129 |  | 1910.0257 |  | 1600 | 10
1024.8269 |  | 2049.6538 |  | 1650 | 10
1116.5838 |  | 2233.1676 |  | 1700 | 10
466.2681 |  | 932.5363 |  | 1750 | 10
509.7501 |  | 1019.5003 |  | 1800 | 10
543.4703 |  | 1086.9406 |  | 1850 | 10
607.7455 |  | 1215.4911 |  | 1900 | 10
667.9 |  | 1335.8 |  | 1950 | 10
732.8 |  | 1465.6 |  | 2000 | 10
774.6 |  | 1549.2 |  | 2050 | 10
813.5 |  | 1627 |  | 2100 | 10
616.3385 |  | 1232.6769 |  | 2150 | 10
707.5905 |  | 1415.1811 |  | 2200 | 10
786.8099 |  | 1573.6198 |  | 2250 | 10
825.5 |  | 1651 |  | 2300 | 10
756.8 |  | 1513.6 |  | 2350 | 10
830.5 |  | 1661 |  | 2400 | 10
873.3 |  | 1746.6 |  | 2450 | 10
639.1572 |  | 1278.3144 |  | 2500 | 12
794.9133 |  | 1589.8266 |  | 2550 | 12
882.342 |  | 1764.6841 |  | 2600 | 12
935.9263 |  | 1871.8526 |  | 2650 | 12
1136.2741 |  | 2272.5482 |  | 2700 | 12
1332.9681 |  | 2665.9362 |  | 2750 | 12
1528.3535 |  | 3056.707 |  | 2800 | 12
626.346 |  | 1252.6919 |  | 2850 | 12
764.9699 |  | 1529.9399 |  | 2900 | 12
682.0481 |  | 1364.0961 |  | 2950 | 12
802.7921 |  | 1605.5841 |  | 3000 | 12
932.9167 |  | 1865.8335 |  | 3050 | 12
1000.0001 |  | 2000.0002 |  | 3100 | 12
753.2463 |  | 1506.4926 |  | 3150 | 12
820.4429 |  | 1640.8858 |  | 3200 | 12
953.3171 |  | 1906.6342 |  | 3250 | 12
1029.7585 |  | 2059.5169 |  | 3300 | 12
1330.3437 |  | 2660.6874 |  | 3350 | 12
1378.5213 |  | 2757.0426 |  | 3400 | 12
1467.9509 |  | 2935.9018 |  | 3450 | 12
844.864 |  | 1689.7279 |  | 3500 | 12
982.3526 |  | 1964.7052 |  | 3550 | 14
1104.8611 |  | 2209.7222 |  | 3600 | 14
1214.4257 |  | 2428.8514 |  | 3650 | 14
1383.6857 |  | 2767.3715 |  | 3700 | 14
1551.2098 |  | 3102.4196 |  | 3750 | 14
1664.6746 |  | 3329.3491 |  | 3800 | 14
840.7876 |  | 1681.5751 |  | 3850 | 14
995.4751 |  | 1990.9502 |  | 3900 | 14
1093.6698 |  | 2187.3397 |  | 3950 | 14
1144.8546 |  | 2289.7092 |  | 4000 | 14
1204.5001 |  | 2409.0002 |  | 4050 | 14
1252.5 |  | 2505 |  | 4100 | 14
648.3835 |  | 1296.767 |  | 4150 | 14
820.3589 |  | 1640.7178 |  | 4200 | 14
941.0352 |  | 1882.0704 |  | 4250 | 16
1045.3157 |  | 2090.6314 |  | 4300 | 16
1136.5096 |  | 2273.0192 |  | 4350 | 16
1235.933 |  | 2471.866 |  | 4400 | 16
1229.0007 |  | 2458.0014 |  | 4450 | 16
1303.9328 |  | 2607.8655 |  | 4500 | 16
1403.874 |  | 2807.748 |  | 4550 | 16
1484.3188 |  | 2968.6376 |  | 4600 | 16
1171.9065 |  | 2343.8131 |  | 4650 | 16
1316.9347 |  | 2633.8694 |  | 4700 | 16
1454.2378 |  | 2908.4756 |  | 4750 | 16
1568.7217 |  | 3137.4434 |  | 4800 | 16
1414.8836 |  | 2829.7672 |  | 4850 | 16
1523.3743 |  | 3046.7486 |  | 4900 | 16
1625.1171 |  | 3250.2342 |  | 4950 | 16
1757.2796 |  | 3514.5593 |  | 5000 | 16
1846.8509 |  | 3693.7017 |  | 5050 | 16
1914.581 |  | 3829.162 |  | 5100 | 16
1634.3829 |  | 3268.7658 |  | 5150 | 16
1915.2738 |  | 3830.5476 |  | 5200 | 16
2165.2718 |  | 4330.5437 |  | 5250 | 16
1914.1469 |  | 3828.2938 |  | 5300 | 16
2017.9874 |  | 4035.9748 |  | 5350 | 16
2141.5995 |  | 4283.199 |  | 5400 | 16
2290.5785 |  | 4581.157 |  | 5450 | 16
1727.4951 |  | 3454.9903 |  | 5500 | 16
1826.6982 |  | 3653.3965 |  | 5550 | 18
2003.3556 |  | 4006.7112 |  | 5600 | 18
2187.1986 |  | 4374.3972 |  | 5650 | 18
2293.6739 |  | 4587.3477 |  | 5700 | 18
2422.2984 |  | 4844.5968 |  | 5750 | 18
2547.3614 |  | 5094.7228 |  | 5800 | 18
2953.0528 |  | 5906.1056 |  | 5850 | 18
3220.9607 |  | 6441.9215 |  | 6000 | 18
3579.8797 |  | 7159.7593 |  | 6150 | 18
3926.8748 |  | 7853.7497 |  | 6300 | 18
4128.2784 |  | 8256.5567 |  | 6450 | 18
120.9035 |  | 362.7105 |  | 6600 | 18
134.1949 |  | 402.5848 |  | 6750 | 18
146.7341 |  | 440.2024 |  | 6900 | 18
154 |  | 462 |  | 7050 | 20
79 |  | 237 |  | 7200 | 20
169.9715 |  | 509.9146 |  | 7350 | 20
191.939 |  | 575.8169 |  | 7500 | 20
226.3257 |  | 678.977 |  | 7650 | 20
124.0691 |  | 372.2073 |  | 7800 | 20
190.191 |  | 570.5729 |  | 7950 | 20
214.0515 |  | 642.1546 |  | 8100 | 20
249.8523 |  | 749.5569 |  | 8250 | 20
243.9916 |  | 731.9747 |  | 8400 | 20
128.156 |  | 384.4681 |  | 8550 | 20
152.95 |  | 458.85 |  | 8700 | 20
168.2305 |  | 504.6915 |  | 8850 | 24
184.528 |  | 553.584 |  | 9000 | 24
191.32 |  | 573.96 |  | 9150 | 24
90.3291 |  | 270.9873 |  | 9300 | 24
95.22 |  | 285.66 |  | 9450 | 24
176.1225 |  | 528.3676 |  | 9600 | 24
200.368 |  | 601.1041 |  | 9750 | 24
232.5586 |  | 697.6759 |  | 9900 | 24
232.5586 |  | 697.6759 |  | 10050 | 24
111.4482 |  | 334.3446 |  | 10200 | 24
118.6369 |  | 355.9106 |  | 10350 | 24
205.3636 |  | 616.0908 |  | 10500 | 24
235.6474 |  | 706.9421 |  | 10650 | 24
257.4 |  | 772.2001 |  | 10800 | 24
277.4627 |  | 832.388 |  | 10950 | 24
300 |  | 900 |  | 11100 | 24
300 |  | 900 |  | 11250 | 24
136.1059 |  | 408.3177 |  | 11400 | 24
162.637 |  | 487.911 |  | 11550 | 24
165.3271 |  | 495.9813 |  | 11700 | 24
271.9533 |  | 815.8599 |  | 11850 | 24
309.3395 |  | 928.0185 |  | 12000 | 24
341.2848 |  | 1023.8543 |  | 12150 | 24
380.858 |  | 1142.5741 |  | 12300 | 24
405.1149 |  | 1215.3446 |  | 12450 | 24
406.8778 |  | 1220.6335 |  | 12600 | 24
154.2292 |  | 462.6875
205.8649 |  | 617.5946
227.7916 |  | 683.3749
294.5625 |  | 883.6876
355.8818 |  | 1067.6453
415.2757 |  | 1245.8272
449.14 |  | 1347.4201
222.9265 |  | 668.7796
339.6329 |  | 1018.8988
384.0902 |  | 1152.2706
424.5536 |  | 1273.6608
491.3603 |  | 1474.0808
551.7418 |  | 1655.2254
573.0512 |  | 1719.1537
179.981 |  | 539.9431
237.9031 |  | 713.7094
284.3868 |  | 853.1603
260.585 |  | 781.755
273.2839 |  | 819.8518
330.9972 |  | 992.9917
524.7552 |  | 1574.2657
534.9404 |  | 1604.8213
573.9449 |  | 1721.8346
599.7227 |  | 1799.168
512.3923 |  | 1537.1769
573.8168 |  | 1721.4503
630.1667 |  | 1890.5
681.695 |  | 2045.085
242.0702 |  | 726.2105
291.6367 |  | 874.91
290.4936 |  | 871.4809
350.6693 |  | 1052.008
375.4803 |  | 1126.4408
402.5638 |  | 1207.6913
427.3855 |  | 1282.1565
430.0891 |  | 1290.2674
453.84 |  | 1361.52
360.7205 |  | 1082.1614
391.3696 |  | 1174.1089
444.5377 |  | 1333.6131
455.5928 |  | 1366.7783
548.8465 |  | 1646.5396
628.8755 |  | 1886.6265
683.4996 |  | 2050.4988
734.2064 |  | 2202.6191
789.7994 |  | 2369.3983
360.84 |  | 1082.52
106.8596 |  | 320.5787
913.8143 |  | 2741.443
969.4037 |  | 2908.2111
1015.343 |  | 3046.0289
1051.8577 |  | 3155.5731
1127.0937 |  | 3381.2812
456.5775 |  | 1369.7324
508.0798 |  | 1524.2394
534.9443 |  | 1604.833
568.82 |  | 1706.46
885.0742 |  | 2655.2225
912.6252 |  | 2737.8756
955.0129 |  | 2865.0386
1024.8269 |  | 3074.4806
1116.5838 |  | 3349.7514
466.2681 |  | 1398.8044
509.7501 |  | 1529.2504
543.4703 |  | 1630.411
607.7455 |  | 1823.2366
667.9 |  | 2003.7
732.8 |  | 2198.4
774.6 |  | 2323.8
813.5 |  | 2440.5
616.3385 |  | 1849.0154
707.5905 |  | 2122.7716
786.8099 |  | 2360.4297
825.5 |  | 2476.5
756.8 |  | 2270.4
830.5 |  | 2491.5
873.3 |  | 2619.9
639.1572 |  | 1917.4715
794.9133 |  | 2384.7399
882.342 |  | 2647.0261
935.9263 |  | 2807.7789
1136.2741 |  | 3408.8222
1332.9681 |  | 3998.9043
1528.3535 |  | 4585.0605
626.346 |  | 1879.0379
764.9699 |  | 2294.9098
682.0481 |  | 2046.1442
802.7921 |  | 2408.3762
932.9167 |  | 2798.7502
1000.0001 |  | 3000.0002
753.2463 |  | 2259.739
820.4429 |  | 2461.3287
953.3171 |  | 2859.9513
1029.7585 |  | 3089.2754
1330.3437 |  | 3991.0312
1378.5213 |  | 4135.5639
1467.9509 |  | 4403.8528
844.864 |  | 2534.5919
982.3526 |  | 2947.0578
1104.8611 |  | 3314.5834
1214.4257 |  | 3643.277
1383.6857 |  | 4151.0572
1551.2098 |  | 4653.6293
1664.6746 |  | 4994.0237
840.7876 |  | 2522.3627
995.4751 |  | 2986.4252
1093.6698 |  | 3281.0095
1144.8546 |  | 3434.5638
1204.5001 |  | 3613.5003
1252.5 |  | 3757.5
648.3835 |  | 1945.1505
820.3589 |  | 2461.0767
941.0352 |  | 2823.1056
1045.3157 |  | 3135.947
1136.5096 |  | 3409.5287
1235.933 |  | 3707.799
1229.0007 |  | 3687.0022
1303.9328 |  | 3911.7983
1403.874 |  | 4211.6221
1484.3188 |  | 4452.9564
1171.9065 |  | 3515.7196
1316.9347 |  | 3950.8041
1454.2378 |  | 4362.7133
1568.7217 |  | 4706.1651
1414.8836 |  | 4244.6507
1523.3743 |  | 4570.123
1625.1171 |  | 4875.3512
1757.2796 |  | 5271.8389
1846.8509 |  | 5540.5526
1914.581 |  | 5743.743
1634.3829 |  | 4903.1487
1915.2738 |  | 5745.8213
2165.2718 |  | 6495.8155
1914.1469 |  | 5742.4408
2017.9874 |  | 6053.9622
2141.5995 |  | 6424.7985
2290.5785 |  | 6871.7355
1727.4951 |  | 5182.4854
1826.6982 |  | 5480.0947
2003.3556 |  | 6010.0669
2187.1986 |  | 6561.5959
2293.6739 |  | 6881.0216
2422.2984 |  | 7266.8952
2547.3614 |  | 7642.0842
2953.0528 |  | 8859.1584
3220.9607 |  | 9662.8822
3579.8797 |  | 10739.639
3926.8748 |  | 11780.6245
4128.2784 |  | 12384.8351
120.9035 |  | 483.6139
134.1949 |  | 536.7797
146.7341 |  | 586.9365
154 |  | 616
79 |  | 316
169.9715 |  | 679.8862
191.939 |  | 767.7559
226.3257 |  | 905.3027
124.0691 |  | 496.2764
190.191 |  | 760.7639
214.0515 |  | 856.2061
249.8523 |  | 999.4092
243.9916 |  | 975.9663
128.156 |  | 512.6241
152.95 |  | 611.8001
168.2305 |  | 672.9221
184.528 |  | 738.1121
191.32 |  | 765.2801
90.3291 |  | 361.3164
95.22 |  | 380.88
176.1225 |  | 704.4902
200.368 |  | 801.4722
232.5586 |  | 930.2345
232.5586 |  | 930.2345
111.4482 |  | 445.7928
118.6369 |  | 474.5474
205.3636 |  | 821.4543
235.6474 |  | 942.5895
257.4 |  | 1029.6001
277.4627 |  | 1109.8506
300 |  | 1200
300 |  | 1200
136.1059 |  | 544.4236
162.637 |  | 650.548
165.3271 |  | 661.3083
271.9533 |  | 1087.8131
309.3395 |  | 1237.358
341.2848 |  | 1365.139
380.858 |  | 1523.4321
405.1149 |  | 1620.4594
406.8778 |  | 1627.5113
154.2292 |  | 616.9167
205.8649 |  | 823.4595
227.7916 |  | 911.1665
294.5625 |  | 1178.2501
355.8818 |  | 1423.5271
415.2757 |  | 1661.103
449.14 |  | 1796.5602
222.9265 |  | 891.7062
339.6329 |  | 1358.5317
384.0902 |  | 1536.3608
424.5536 |  | 1698.2144
491.3603 |  | 1965.4411
551.7418 |  | 2206.9672
573.0512 |  | 2292.2049
179.981 |  | 719.9241
237.9031 |  | 951.6126
284.3868 |  | 1137.547
260.585 |  | 1042.34
273.2839 |  | 1093.1357
330.9972 |  | 1323.9889
524.7552 |  | 2099.021
534.9404 |  | 2139.7617
573.9449 |  | 2295.7795
599.7227 |  | 2398.8907
512.3923 |  | 2049.5692
573.8168 |  | 2295.2671
630.1667 |  | 2520.6667
681.695 |  | 2726.78
242.0702 |  | 968.2806
291.6367 |  | 1166.5466
290.4936 |  | 1161.9746
350.6693 |  | 1402.6774
375.4803 |  | 1501.921
402.5638 |  | 1610.2551
427.3855 |  | 1709.542
430.0891 |  | 1720.3565
453.84 |  | 1815.36
360.7205 |  | 1442.8819
391.3696 |  | 1565.4785
444.5377 |  | 1778.1508
455.5928 |  | 1822.371
548.8465 |  | 2195.3862
628.8755 |  | 2515.502
683.4996 |  | 2733.9985
734.2064 |  | 2936.8255
789.7994 |  | 3159.1977
360.84 |  | 1443.36
106.8596 |  | 427.4383
913.8143 |  | 3655.2573
969.4037 |  | 3877.6149
1015.343 |  | 4061.3719
1051.8577 |  | 4207.4307
1127.0937 |  | 4508.3749
456.5775 |  | 1826.3098
508.0798 |  | 2032.3192
534.9443 |  | 2139.7774
568.82 |  | 2275.28
885.0742 |  | 3540.2967
912.6252 |  | 3650.5009
955.0129 |  | 3820.0514
1024.8269 |  | 4099.3075
1116.5838 |  | 4466.3352
466.2681 |  | 1865.0725
509.7501 |  | 2039.0006
543.4703 |  | 2173.8813
607.7455 |  | 2430.9822
667.9 |  | 2671.6
732.8 |  | 2931.2
774.6 |  | 3098.4
813.5 |  | 3254
616.3385 |  | 2465.3539
707.5905 |  | 2830.3621
786.8099 |  | 3147.2397
825.5 |  | 3302
756.8 |  | 3027.2
830.5 |  | 3322
873.3 |  | 3493.2
639.1572 |  | 2556.6287
794.9133 |  | 3179.6532
882.342 |  | 3529.3682
935.9263 |  | 3743.7052
1136.2741 |  | 4545.0963
1332.9681 |  | 5331.8724
1528.3535 |  | 6113.414
626.346 |  | 2505.3838
764.9699 |  | 3059.8797
682.0481 |  | 2728.1922
802.7921 |  | 3211.1683
932.9167 |  | 3731.667
1000.0001 |  | 4000.0003
753.2463 |  | 3012.9853
820.4429 |  | 3281.7717
953.3171 |  | 3813.2684
1029.7585 |  | 4119.0339
1330.3437 |  | 5321.3749
1378.5213 |  | 5514.0852
1467.9509 |  | 5871.8037
844.864 |  | 3379.4558
982.3526 |  | 3929.4104
1104.8611 |  | 4419.4445
1214.4257 |  | 4857.7027
1383.6857 |  | 5534.743
1551.2098 |  | 6204.8391
1664.6746 |  | 6658.6983
840.7876 |  | 3363.1503
995.4751 |  | 3981.9003
1093.6698 |  | 4374.6794
1144.8546 |  | 4579.4184
1204.5001 |  | 4818.0004
1252.5 |  | 5010
648.3835 |  | 2593.534
820.3589 |  | 3281.4355
941.0352 |  | 3764.1408
1045.3157 |  | 4181.2627
1136.5096 |  | 4546.0383
1235.933 |  | 4943.7321
1229.0007 |  | 4916.0029
1303.9328 |  | 5215.731
1403.874 |  | 5615.4961
1484.3188 |  | 5937.2753
1171.9065 |  | 4687.6261
1316.9347 |  | 5267.7388
1454.2378 |  | 5816.9511
1568.7217 |  | 6274.8868
1414.8836 |  | 5659.5343
1523.3743 |  | 6093.4973
1625.1171 |  | 6500.4683
1757.2796 |  | 7029.1185
1846.8509 |  | 7387.4035
1914.581 |  | 7658.324
1634.3829 |  | 6537.5317
1915.2738 |  | 7661.0951
2165.2718 |  | 8661.0874
1914.1469 |  | 7656.5877
2017.9874 |  | 8071.9496
2141.5995 |  | 8566.398
2290.5785 |  | 9162.314
1727.4951 |  | 6909.9805
1826.6982 |  | 7306.7929
2003.3556 |  | 8013.4225
2187.1986 |  | 8748.7945
2293.6739 |  | 9174.6955
2422.2984 |  | 9689.1937
2547.3614 |  | 10189.4456
2953.0528 |  | 11812.2111
3220.9607 |  | 12883.8429
3579.8797 |  | 14319.5187
3926.8748 |  | 15707.4993
4128.2784 |  | 16513.1135
120.9035 |  | 120.9035
134.1949 |  | 134.1949
146.7341 |  | 146.7341
154 |  | 154
79 |  | 79
169.9715 |  | 169.9715
191.939 |  | 191.939
226.3257 |  | 226.3257
124.0691 |  | 124.0691
190.191 |  | 190.191
214.0515 |  | 214.0515
249.8523 |  | 249.8523
243.9916 |  | 243.9916
128.156 |  | 128.156
152.95 |  | 152.95
168.2305 |  | 168.2305
184.528 |  | 184.528
191.32 |  | 191.32
90.3291 |  | 90.3291
95.22 |  | 95.22
176.1225 |  | 176.1225
200.368 |  | 200.368
232.5586 |  | 232.5586
232.5586 |  | 232.5586
111.4482 |  | 111.4482
118.6369 |  | 118.6369
205.3636 |  | 205.3636
235.6474 |  | 235.6474
257.4 |  | 257.4
277.4627 |  | 277.4627
300 |  | 300
300 |  | 300
136.1059 |  | 136.1059
162.637 |  | 162.637
165.3271 |  | 165.3271
271.9533 |  | 271.9533
309.3395 |  | 309.3395
341.2848 |  | 341.2848
380.858 |  | 380.858
405.1149 |  | 405.1149
406.8778 |  | 406.8778
154.2292 |  | 154.2292
205.8649 |  | 205.8649
227.7916 |  | 227.7916
294.5625 |  | 294.5625
355.8818 |  | 355.8818
415.2757 |  | 415.2757
449.14 |  | 449.14
222.9265 |  | 222.9265
339.6329 |  | 339.6329
384.0902 |  | 384.0902
424.5536 |  | 424.5536
491.3603 |  | 491.3603
551.7418 |  | 551.7418
573.0512 |  | 573.0512
179.981 |  | 179.981
237.9031 |  | 237.9031
284.3868 |  | 284.3868
260.585 |  | 260.585
273.2839 |  | 273.2839
330.9972 |  | 330.9972
524.7552 |  | 524.7552
534.9404 |  | 534.9404
573.9449 |  | 573.9449
599.7227 |  | 599.7227
512.3923 |  | 512.3923
573.8168 |  | 573.8168
630.1667 |  | 630.1667
681.695 |  | 681.695
242.0702 |  | 242.0702
291.6367 |  | 291.6367
290.4936 |  | 290.4936
350.6693 |  | 350.6693
375.4803 |  | 375.4803
402.5638 |  | 402.5638
427.3855 |  | 427.3855
430.0891 |  | 430.0891
453.84 |  | 453.84
360.7205 |  | 360.7205
391.3696 |  | 391.3696
444.5377 |  | 444.5377
455.5928 |  | 455.5928
548.8465 |  | 548.8465
628.8755 |  | 628.8755
683.4996 |  | 683.4996
734.2064 |  | 734.2064
789.7994 |  | 789.7994
360.84 |  | 360.84
106.8596 |  | 106.8596
913.8143 |  | 913.8143
969.4037 |  | 969.4037
1015.343 |  | 1015.343
1051.8577 |  | 1051.8577
1127.0937 |  | 1127.0937
456.5775 |  | 456.5775
508.0798 |  | 508.0798
534.9443 |  | 534.9443
568.82 |  | 568.82
885.0742 |  | 885.0742
912.6252 |  | 912.6252
955.0129 |  | 955.0129
1024.8269 |  | 1024.8269
1116.5838 |  | 1116.5838
466.2681 |  | 466.2681
509.7501 |  | 509.7501
543.4703 |  | 543.4703
607.7455 |  | 607.7455
667.9 |  | 667.9
732.8 |  | 732.8
774.6 |  | 774.6
813.5 |  | 813.5
616.3385 |  | 616.3385
707.5905 |  | 707.5905
786.8099 |  | 786.8099
825.5 |  | 825.5
756.8 |  | 756.8
830.5 |  | 830.5
873.3 |  | 873.3
639.1572 |  | 639.1572
794.9133 |  | 794.9133
882.342 |  | 882.342
935.9263 |  | 935.9263
1136.2741 |  | 1136.2741
1332.9681 |  | 1332.9681
1528.3535 |  | 1528.3535
626.346 |  | 626.346
764.9699 |  | 764.9699
682.0481 |  | 682.0481
802.7921 |  | 802.7921
932.9167 |  | 932.9167
1000.0001 |  | 1000.0001
753.2463 |  | 753.2463
820.4429 |  | 820.4429
953.3171 |  | 953.3171
1029.7585 |  | 1029.7585
1330.3437 |  | 1330.3437
1378.5213 |  | 1378.5213
1467.9509 |  | 1467.9509
844.864 |  | 844.864
982.3526 |  | 982.3526
1104.8611 |  | 1104.8611
1214.4257 |  | 1214.4257
1383.6857 |  | 1383.6857
1551.2098 |  | 1551.2098
1664.6746 |  | 1664.6746
840.7876 |  | 840.7876
995.4751 |  | 995.4751
1093.6698 |  | 1093.6698
1144.8546 |  | 1144.8546
1204.5001 |  | 1204.5001
1252.5 |  | 1252.5
648.3835 |  | 648.3835
820.3589 |  | 820.3589
941.0352 |  | 941.0352
1045.3157 |  | 1045.3157
1136.5096 |  | 1136.5096
1235.933 |  | 1235.933
1229.0007 |  | 1229.0007
1303.9328 |  | 1303.9328
1403.874 |  | 1403.874
1484.3188 |  | 1484.3188
1171.9065 |  | 1171.9065
1316.9347 |  | 1316.9347
1454.2378 |  | 1454.2378
1568.7217 |  | 1568.7217
1414.8836 |  | 1414.8836
1523.3743 |  | 1523.3743
1625.1171 |  | 1625.1171
1757.2796 |  | 1757.2796
1846.8509 |  | 1846.8509
1914.581 |  | 1914.581
1634.3829 |  | 1634.3829
1915.2738 |  | 1915.2738
2165.2718 |  | 2165.2718
1914.1469 |  | 1914.1469
2017.9874 |  | 2017.9874
2141.5995 |  | 2141.5995
2290.5785 |  | 2290.5785
1727.4951 |  | 1727.4951
1826.6982 |  | 1826.6982
2003.3556 |  | 2003.3556
2187.1986 |  | 2187.1986
2293.6739 |  | 2293.6739
2422.2984 |  | 2422.2984
2547.3614 |  | 2547.3614
2953.0528 |  | 2953.0528
3220.9607 |  | 3220.9607
3579.8797 |  | 3579.8797
3926.8748 |  | 3926.8748
4128.2784 |  | 4128.2784
120.9035 |  | 241.807
134.1949 |  | 268.3898
146.7341 |  | 293.4682
154 |  | 308
79 |  | 158
169.9715 |  | 339.9431
191.939 |  | 383.8779
226.3257 |  | 452.6514
124.0691 |  | 248.1382
190.191 |  | 380.3819
214.0515 |  | 428.1031
249.8523 |  | 499.7046
243.9916 |  | 487.9832
128.156 |  | 256.3121
152.95 |  | 305.9
168.2305 |  | 336.461
184.528 |  | 369.056
191.32 |  | 382.64
90.3291 |  | 180.6582
95.22 |  | 190.44
176.1225 |  | 352.2451
200.368 |  | 400.7361
232.5586 |  | 465.1173
232.5586 |  | 465.1173
111.4482 |  | 222.8964
118.6369 |  | 237.2737
205.3636 |  | 410.7272
235.6474 |  | 471.2947
257.4 |  | 514.8
277.4627 |  | 554.9253
300 |  | 600
300 |  | 600
136.1059 |  | 272.2118
162.637 |  | 325.274
165.3271 |  | 330.6542
271.9533 |  | 543.9066
309.3395 |  | 618.679
341.2848 |  | 682.5695
380.858 |  | 761.716
405.1149 |  | 810.2297
406.8778 |  | 813.7556
154.2292 |  | 308.4583
205.8649 |  | 411.7298
227.7916 |  | 455.5833
294.5625 |  | 589.1251
355.8818 |  | 711.7636
415.2757 |  | 830.5515
449.14 |  | 898.2801
222.9265 |  | 445.8531
339.6329 |  | 679.2659
384.0902 |  | 768.1804
424.5536 |  | 849.1072
491.3603 |  | 982.7205
551.7418 |  | 1103.4836
573.0512 |  | 1146.1024
179.981 |  | 359.9621
237.9031 |  | 475.8063
284.3868 |  | 568.7735
260.585 |  | 521.17
273.2839 |  | 546.5679
330.9972 |  | 661.9944
524.7552 |  | 1049.5105
534.9404 |  | 1069.8809
573.9449 |  | 1147.8898
599.7227 |  | 1199.4453
512.3923 |  | 1024.7846
573.8168 |  | 1147.6336
630.1667 |  | 1260.3334
681.695 |  | 1363.39
242.0702 |  | 484.1403
291.6367 |  | 583.2733
290.4936 |  | 580.9873
350.6693 |  | 701.3387
375.4803 |  | 750.9605
402.5638 |  | 805.1276
427.3855 |  | 854.771
430.0891 |  | 860.1783
453.84 |  | 907.68
360.7205 |  | 721.4409
391.3696 |  | 782.7393
444.5377 |  | 889.0754
455.5928 |  | 911.1855
548.8465 |  | 1097.6931
628.8755 |  | 1257.751
683.4996 |  | 1366.9992
734.2064 |  | 1468.4128
789.7994 |  | 1579.5988
360.84 |  | 721.68
106.8596 |  | 213.7192
913.8143 |  | 1827.6287
969.4037 |  | 1938.8074
1015.343 |  | 2030.6859
1051.8577 |  | 2103.7154
1127.0937 |  | 2254.1875
456.5775 |  | 913.1549
508.0798 |  | 1016.1596
534.9443 |  | 1069.8887
568.82 |  | 1137.64
885.0742 |  | 1770.1484
912.6252 |  | 1825.2504
955.0129 |  | 1910.0257
1024.8269 |  | 2049.6538
1116.5838 |  | 2233.1676
466.2681 |  | 932.5363
509.7501 |  | 1019.5003
543.4703 |  | 1086.9406
607.7455 |  | 1215.4911
667.9 |  | 1335.8
732.8 |  | 1465.6
774.6 |  | 1549.2
813.5 |  | 1627
616.3385 |  | 1232.6769
707.5905 |  | 1415.1811
786.8099 |  | 1573.6198
825.5 |  | 1651
756.8 |  | 1513.6
830.5 |  | 1661
873.3 |  | 1746.6
639.1572 |  | 1278.3144
794.9133 |  | 1589.8266
882.342 |  | 1764.6841
935.9263 |  | 1871.8526
1136.2741 |  | 2272.5482
1332.9681 |  | 2665.9362
1528.3535 |  | 3056.707
626.346 |  | 1252.6919
764.9699 |  | 1529.9399
682.0481 |  | 1364.0961
802.7921 |  | 1605.5841
932.9167 |  | 1865.8335
1000.0001 |  | 2000.0002
753.2463 |  | 1506.4926
820.4429 |  | 1640.8858
953.3171 |  | 1906.6342
1029.7585 |  | 2059.5169
1330.3437 |  | 2660.6874
1378.5213 |  | 2757.0426
1467.9509 |  | 2935.9018
844.864 |  | 1689.7279
982.3526 |  | 1964.7052
1104.8611 |  | 2209.7222
1214.4257 |  | 2428.8514
1383.6857 |  | 2767.3715
1551.2098 |  | 3102.4196
1664.6746 |  | 3329.3491
840.7876 |  | 1681.5751
995.4751 |  | 1990.9502
1093.6698 |  | 2187.3397
1144.8546 |  | 2289.7092
1204.5001 |  | 2409.0002
1252.5 |  | 2505
648.3835 |  | 1296.767
820.3589 |  | 1640.7178
941.0352 |  | 1882.0704
1045.3157 |  | 2090.6314
1136.5096 |  | 2273.0192
1235.933 |  | 2471.866
1229.0007 |  | 2458.0014
1303.9328 |  | 2607.8655
1403.874 |  | 2807.748
1484.3188 |  | 2968.6376
1171.9065 |  | 2343.8131
1316.9347 |  | 2633.8694
1454.2378 |  | 2908.4756
1568.7217 |  | 3137.4434
1414.8836 |  | 2829.7672
1523.3743 |  | 3046.7486
1625.1171 |  | 3250.2342
1757.2796 |  | 3514.5593
1846.8509 |  | 3693.7017
1914.581 |  | 3829.162
1634.3829 |  | 3268.7658
1915.2738 |  | 3830.5476
2165.2718 |  | 4330.5437
1914.1469 |  | 3828.2938
2017.9874 |  | 4035.9748
2141.5995 |  | 4283.199
2290.5785 |  | 4581.157
1727.4951 |  | 3454.9903
1826.6982 |  | 3653.3965
2003.3556 |  | 4006.7112
2187.1986 |  | 4374.3972
2293.6739 |  | 4587.3477
2422.2984 |  | 4844.5968
2547.3614 |  | 5094.7228
2953.0528 |  | 5906.1056
3220.9607 |  | 6441.9215
3579.8797 |  | 7159.7593
3926.8748 |  | 7853.7497
4128.2784 |  | 8256.5567
120.9035 |  | 362.7105
134.1949 |  | 402.5848
146.7341 |  | 440.2024
154 |  | 462
79 |  | 237
169.9715 |  | 509.9146
191.939 |  | 575.8169
226.3257 |  | 678.977
124.0691 |  | 372.2073
190.191 |  | 570.5729
214.0515 |  | 642.1546
249.8523 |  | 749.5569
243.9916 |  | 731.9747
128.156 |  | 384.4681
152.95 |  | 458.85
168.2305 |  | 504.6915
184.528 |  | 553.584
191.32 |  | 573.96
90.3291 |  | 270.9873
95.22 |  | 285.66
176.1225 |  | 528.3676
200.368 |  | 601.1041
232.5586 |  | 697.6759
232.5586 |  | 697.6759
111.4482 |  | 334.3446
118.6369 |  | 355.9106
205.3636 |  | 616.0908
235.6474 |  | 706.9421
257.4 |  | 772.2001
277.4627 |  | 832.388
300 |  | 900
300 |  | 900
136.1059 |  | 408.3177
162.637 |  | 487.911
165.3271 |  | 495.9813
271.9533 |  | 815.8599
309.3395 |  | 928.0185
341.2848 |  | 1023.8543
380.858 |  | 1142.5741
405.1149 |  | 1215.3446
406.8778 |  | 1220.6335
154.2292 |  | 462.6875
205.8649 |  | 617.5946
227.7916 |  | 683.3749
294.5625 |  | 883.6876
355.8818 |  | 1067.6453
415.2757 |  | 1245.8272
449.14 |  | 1347.4201
222.9265 |  | 668.7796
339.6329 |  | 1018.8988
384.0902 |  | 1152.2706
424.5536 |  | 1273.6608
491.3603 |  | 1474.0808
551.7418 |  | 1655.2254
573.0512 |  | 1719.1537
179.981 |  | 539.9431
237.9031 |  | 713.7094
284.3868 |  | 853.1603
260.585 |  | 781.755
273.2839 |  | 819.8518
330.9972 |  | 992.9917
524.7552 |  | 1574.2657
534.9404 |  | 1604.8213
573.9449 |  | 1721.8346
599.7227 |  | 1799.168
512.3923 |  | 1537.1769
573.8168 |  | 1721.4503
630.1667 |  | 1890.5
681.695 |  | 2045.085
242.0702 |  | 726.2105
291.6367 |  | 874.91
290.4936 |  | 871.4809
350.6693 |  | 1052.008
375.4803 |  | 1126.4408
402.5638 |  | 1207.6913
427.3855 |  | 1282.1565
430.0891 |  | 1290.2674
453.84 |  | 1361.52
360.7205 |  | 1082.1614
391.3696 |  | 1174.1089
444.5377 |  | 1333.6131
455.5928 |  | 1366.7783
548.8465 |  | 1646.5396
628.8755 |  | 1886.6265
683.4996 |  | 2050.4988
734.2064 |  | 2202.6191
789.7994 |  | 2369.3983
360.84 |  | 1082.52
106.8596 |  | 320.5787
913.8143 |  | 2741.443
969.4037 |  | 2908.2111
1015.343 |  | 3046.0289
1051.8577 |  | 3155.5731
1127.0937 |  | 3381.2812
456.5775 |  | 1369.7324
508.0798 |  | 1524.2394
534.9443 |  | 1604.833
568.82 |  | 1706.46
885.0742 |  | 2655.2225
912.6252 |  | 2737.8756
955.0129 |  | 2865.0386
1024.8269 |  | 3074.4806
1116.5838 |  | 3349.7514
466.2681 |  | 1398.8044
509.7501 |  | 1529.2504
543.4703 |  | 1630.411
607.7455 |  | 1823.2366
667.9 |  | 2003.7
732.8 |  | 2198.4
774.6 |  | 2323.8
813.5 |  | 2440.5
616.3385 |  | 1849.0154
707.5905 |  | 2122.7716
786.8099 |  | 2360.4297
825.5 |  | 2476.5
756.8 |  | 2270.4
830.5 |  | 2491.5
873.3 |  | 2619.9
639.1572 |  | 1917.4715
794.9133 |  | 2384.7399
882.342 |  | 2647.0261
935.9263 |  | 2807.7789
1136.2741 |  | 3408.8222
1332.9681 |  | 3998.9043
1528.3535 |  | 4585.0605
626.346 |  | 1879.0379
764.9699 |  | 2294.9098
682.0481 |  | 2046.1442
802.7921 |  | 2408.3762
932.9167 |  | 2798.7502
1000.0001 |  | 3000.0002
753.2463 |  | 2259.739
820.4429 |  | 2461.3287
953.3171 |  | 2859.9513
1029.7585 |  | 3089.2754
1330.3437 |  | 3991.0312
1378.5213 |  | 4135.5639
1467.9509 |  | 4403.8528
844.864 |  | 2534.5919
982.3526 |  | 2947.0578
1104.8611 |  | 3314.5834
1214.4257 |  | 3643.277
1383.6857 |  | 4151.0572
1551.2098 |  | 4653.6293
1664.6746 |  | 4994.0237
840.7876 |  | 2522.3627
995.4751 |  | 2986.4252
1093.6698 |  | 3281.0095
1144.8546 |  | 3434.5638
1204.5001 |  | 3613.5003
1252.5 |  | 3757.5
648.3835 |  | 1945.1505
820.3589 |  | 2461.0767
941.0352 |  | 2823.1056
1045.3157 |  | 3135.947
1136.5096 |  | 3409.5287
1235.933 |  | 3707.799
1229.0007 |  | 3687.0022
1303.9328 |  | 3911.7983
1403.874 |  | 4211.6221
1484.3188 |  | 4452.9564
1171.9065 |  | 3515.7196
1316.9347 |  | 3950.8041
1454.2378 |  | 4362.7133
1568.7217 |  | 4706.1651
1414.8836 |  | 4244.6507
1523.3743 |  | 4570.123
1625.1171 |  | 4875.3512
1757.2796 |  | 5271.8389
1846.8509 |  | 5540.5526
1914.581 |  | 5743.743
1634.3829 |  | 4903.1487
1915.2738 |  | 5745.8213
2165.2718 |  | 6495.8155
1914.1469 |  | 5742.4408
2017.9874 |  | 6053.9622
2141.5995 |  | 6424.7985
2290.5785 |  | 6871.7355
1727.4951 |  | 5182.4854
1826.6982 |  | 5480.0947
2003.3556 |  | 6010.0669
2187.1986 |  | 6561.5959
2293.6739 |  | 6881.0216
2422.2984 |  | 7266.8952
2547.3614 |  | 7642.0842
2953.0528 |  | 8859.1584
3220.9607 |  | 9662.8822
3579.8797 |  | 10739.639
3926.8748 |  | 11780.6245
4128.2784 |  | 12384.8351
120.9035 |  | 241.807
134.1949 |  | 268.3898
146.7341 |  | 293.4682
154 |  | 308
79 |  | 158
169.9715 |  | 339.9431
191.939 |  | 383.8779
226.3257 |  | 452.6514
124.0691 |  | 248.1382
190.191 |  | 380.3819
214.0515 |  | 428.1031
249.8523 |  | 499.7046
243.9916 |  | 487.9832
128.156 |  | 256.3121
152.95 |  | 305.9
168.2305 |  | 336.461
184.528 |  | 369.056
191.32 |  | 382.64
90.3291 |  | 180.6582
95.22 |  | 190.44
176.1225 |  | 352.2451
200.368 |  | 400.7361
232.5586 |  | 465.1173
232.5586 |  | 465.1173
111.4482 |  | 222.8964
118.6369 |  | 237.2737
205.3636 |  | 410.7272
235.6474 |  | 471.2947
257.4 |  | 514.8
277.4627 |  | 554.9253
300 |  | 600
300 |  | 600
136.1059 |  | 272.2118
162.637 |  | 325.274
165.3271 |  | 330.6542
271.9533 |  | 543.9066
309.3395 |  | 618.679
341.2848 |  | 682.5695
380.858 |  | 761.716
405.1149 |  | 810.2297
406.8778 |  | 813.7556
154.2292 |  | 308.4583
205.8649 |  | 411.7298
227.7916 |  | 455.5833
294.5625 |  | 589.1251
355.8818 |  | 711.7636
415.2757 |  | 830.5515
449.14 |  | 898.2801
222.9265 |  | 445.8531
339.6329 |  | 679.2659
384.0902 |  | 768.1804
424.5536 |  | 849.1072
491.3603 |  | 982.7205
551.7418 |  | 1103.4836
573.0512 |  | 1146.1024
179.981 |  | 359.9621
237.9031 |  | 475.8063
284.3868 |  | 568.7735
260.585 |  | 521.17
273.2839 |  | 546.5679
330.9972 |  | 661.9944
524.7552 |  | 1049.5105
534.9404 |  | 1069.8809
573.9449 |  | 1147.8898
599.7227 |  | 1199.4453
512.3923 |  | 1024.7846
573.8168 |  | 1147.6336
630.1667 |  | 1260.3334
681.695 |  | 1363.39
242.0702 |  | 484.1403
291.6367 |  | 583.2733
290.4936 |  | 580.9873
350.6693 |  | 701.3387
375.4803 |  | 750.9605
402.5638 |  | 805.1276
427.3855 |  | 854.771
430.0891 |  | 860.1783
453.84 |  | 907.68
360.7205 |  | 721.4409
391.3696 |  | 782.7393
444.5377 |  | 889.0754
455.5928 |  | 911.1855
548.8465 |  | 1097.6931
628.8755 |  | 1257.751
683.4996 |  | 1366.9992
734.2064 |  | 1468.4128
789.7994 |  | 1579.5988
360.84 |  | 721.68
106.8596 |  | 213.7192
913.8143 |  | 1827.6287
969.4037 |  | 1938.8074
1015.343 |  | 2030.6859
1051.8577 |  | 2103.7154
1127.0937 |  | 2254.1875
456.5775 |  | 913.1549
508.0798 |  | 1016.1596
534.9443 |  | 1069.8887
568.82 |  | 1137.64
885.0742 |  | 1770.1484
912.6252 |  | 1825.2504
955.0129 |  | 1910.0257
1024.8269 |  | 2049.6538
1116.5838 |  | 2233.1676
466.2681 |  | 932.5363
509.7501 |  | 1019.5003
543.4703 |  | 1086.9406
607.7455 |  | 1215.4911
667.9 |  | 1335.8
732.8 |  | 1465.6
774.6 |  | 1549.2
813.5 |  | 1627
616.3385 |  | 1232.6769
707.5905 |  | 1415.1811
786.8099 |  | 1573.6198
825.5 |  | 1651
756.8 |  | 1513.6
830.5 |  | 1661
873.3 |  | 1746.6
639.1572 |  | 1278.3144
794.9133 |  | 1589.8266
882.342 |  | 1764.6841
935.9263 |  | 1871.8526
1136.2741 |  | 2272.5482
1332.9681 |  | 2665.9362
1528.3535 |  | 3056.707
626.346 |  | 1252.6919
764.9699 |  | 1529.9399
682.0481 |  | 1364.0961
802.7921 |  | 1605.5841
932.9167 |  | 1865.8335
1000.0001 |  | 2000.0002
753.2463 |  | 1506.4926
820.4429 |  | 1640.8858
953.3171 |  | 1906.6342
1029.7585 |  | 2059.5169
1330.3437 |  | 2660.6874
1378.5213 |  | 2757.0426
1467.9509 |  | 2935.9018
844.864 |  | 1689.7279
982.3526 |  | 1964.7052
1104.8611 |  | 2209.7222
1214.4257 |  | 2428.8514
1383.6857 |  | 2767.3715
1551.2098 |  | 3102.4196
1664.6746 |  | 3329.3491
840.7876 |  | 1681.5751
995.4751 |  | 1990.9502
1093.6698 |  | 2187.3397
1144.8546 |  | 2289.7092
1204.5001 |  | 2409.0002
1252.5 |  | 2505
648.3835 |  | 1296.767
820.3589 |  | 1640.7178
941.0352 |  | 1882.0704
1045.3157 |  | 2090.6314
1136.5096 |  | 2273.0192
1235.933 |  | 2471.866
1229.0007 |  | 2458.0014
1303.9328 |  | 2607.8655
1403.874 |  | 2807.748
1484.3188 |  | 2968.6376
1171.9065 |  | 2343.8131
1316.9347 |  | 2633.8694
1454.2378 |  | 2908.4756
1568.7217 |  | 3137.4434
1414.8836 |  | 2829.7672
1523.3743 |  | 3046.7486
1625.1171 |  | 3250.2342
1757.2796 |  | 3514.5593
1846.8509 |  | 3693.7017
1914.581 |  | 3829.162
1634.3829 |  | 3268.7658
1915.2738 |  | 3830.5476
2165.2718 |  | 4330.5437
1914.1469 |  | 3828.2938
2017.9874 |  | 4035.9748
2141.5995 |  | 4283.199
2290.5785 |  | 4581.157
1727.4951 |  | 3454.9903
1826.6982 |  | 3653.3965
2003.3556 |  | 4006.7112
2187.1986 |  | 4374.3972
2293.6739 |  | 4587.3477
2422.2984 |  | 4844.5968
2547.3614 |  | 5094.7228
2953.0528 |  | 5906.1056
3220.9607 |  | 6441.9215
3579.8797 |  | 7159.7593
3926.8748 |  | 7853.7497
4128.2784 |  | 8256.5567

## Max flow to diameter_Completed
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.)
120.9035 | 2.5 | 241.807 | 4
134.1949 | 3 | 268.3898 | 4
146.7341 | 3 | 293.4682 | 4
154 | 3 | 308 | 4
79 | 2 | 158 | 3
169.9715 | 3 | 339.9431 | 4
191.939 | 3 | 383.8779 | 4
226.3257 | 4 | 452.6514 | 5
124.0691 | 2.5 | 248.1382 | 4
190.191 | 3 | 380.3819 | 4
214.0515 | 3 | 428.1031 | 5
249.8523 | 4 | 499.7046 | 5
243.9916 | 4 | 487.9832 | 5
128.156 | 3 | 256.3121 | 4
152.95 | 3 | 305.9 | 4
168.2305 | 3 | 336.461 | 4
184.528 | 3 | 369.056 | 4
191.32 | 3 | 382.64 | 4
90.3291 | 2.5 | 180.6582 | 3
95.22 | 2.5 | 190.44 | 3
176.1225 | 3 | 352.2451 | 4
200.368 | 3 | 400.7361 | 5
232.5586 | 4 | 465.1173 | 5
232.5586 | 4 | 465.1173 | 5
111.4482 | 2.5 | 222.8964 | 4
118.6369 | 2.5 | 237.2737 | 4
205.3636 | 3 | 410.7272 | 5
235.6474 | 4 | 471.2947 | 5
257.4 | 4 | 514.8 | 5
277.4627 | 4 | 554.9253 | 5
300 | 4 | 600 | 5
300 | 4 | 600 | 5
136.1059 | 3 | 272.2118 | 4
162.637 | 3 | 325.274 | 4
165.3271 | 3 | 330.6542 | 4
271.9533 | 4 | 543.9066 | 5
309.3395 | 4 | 618.679 | 5
341.2848 | 4 | 682.5695 | 6
380.858 | 4 | 761.716 | 6
405.1149 | 5 | 810.2297 | 6
406.8778 | 5 | 813.7556 | 6
154.2292 | 3 | 308.4583 | 4
205.8649 | 3 | 411.7298 | 5
227.7916 | 4 | 455.5833 | 5
294.5625 | 4 | 589.1251 | 5
355.8818 | 4 | 711.7636 | 6
415.2757 | 5 | 830.5515 | 6
449.14 | 5 | 898.2801 | 6
222.9265 | 4 | 445.8531 | 5
339.6329 | 4 | 679.2659 | 6
384.0902 | 4 | 768.1804 | 6
424.5536 | 5 | 849.1072 | 6
491.3603 | 5 | 982.7205 | 8
551.7418 | 5 | 1103.4836 | 8
573.0512 | 5 | 1146.1024 | 8
179.981 | 3 | 359.9621 | 4
237.9031 | 4 | 475.8063 | 5
284.3868 | 4 | 568.7735 | 5
260.585 | 4 | 521.17 | 5
273.2839 | 4 | 546.5679 | 5
330.9972 | 4 | 661.9944 | 6
524.7552 | 5 | 1049.5105 | 8
534.9404 | 5 | 1069.8809 | 8
573.9449 | 5 | 1147.8898 | 8
599.7227 | 5 | 1199.4453 | 8
512.3923 | 5 | 1024.7846 | 8
573.8168 | 5 | 1147.6336 | 8
630.1667 | 5 | 1260.3334 | 8
681.695 | 6 | 1363.39 | 8
242.0702 | 4 | 484.1403 | 5
291.6367 | 4 | 583.2733 | 5
290.4936 | 4 | 580.9873 | 5
350.6693 | 4 | 701.3387 | 6
375.4803 | 4 | 750.9605 | 6
402.5638 | 5 | 805.1276 | 6
427.3855 | 5 | 854.771 | 6
430.0891 | 5 | 860.1783 | 6
453.84 | 5 | 907.68 | 6
360.7205 | 4 | 721.4409 | 6
391.3696 | 4 | 782.7393 | 6
444.5377 | 5 | 889.0754 | 6
455.5928 | 5 | 911.1855 | 6
548.8465 | 5 | 1097.6931 | 8
628.8755 | 5 | 1257.751 | 8
683.4996 | 6 | 1366.9992 | 8
734.2064 | 6 | 1468.4128 | 8
789.7994 | 6 | 1579.5988 | 8
360.84 | 4 | 721.68 | 6
106.8596 | 2.5 | 213.7192 | 3
913.8143 | 6 | 1827.6287 | 10
969.4037 | 8 | 1938.8074 | 10
1015.343 | 8 | 2030.6859 | 10
1051.8577 | 8 | 2103.7154 | 10
1127.0937 | 8 | 2254.1875 | 10
456.5775 | 5 | 913.1549 | 6
508.0798 | 5 | 1016.1596 | 8
534.9443 | 5 | 1069.8887 | 8
568.82 | 5 | 1137.64 | 8
885.0742 | 6 | 1770.1484 | 10
912.6252 | 6 | 1825.2504 | 10
955.0129 | 8 | 1910.0257 | 10
1024.8269 | 8 | 2049.6538 | 10
1116.5838 | 8 | 2233.1676 | 10
466.2681 | 5 | 932.5363 | 6
509.7501 | 5 | 1019.5003 | 8
543.4703 | 5 | 1086.9406 | 8
607.7455 | 5 | 1215.4911 | 8
667.9 | 6 | 1335.8 | 8
732.8 | 6 | 1465.6 | 8
774.6 | 6 | 1549.2 | 8
813.5 | 6 | 1627 | 10
616.3385 | 5 | 1232.6769 | 8
707.5905 | 6 | 1415.1811 | 8
786.8099 | 6 | 1573.6198 | 8
825.5 | 6 | 1651 | 10
756.8 | 6 | 1513.6 | 8
830.5 | 6 | 1661 | 10
873.3 | 6 | 1746.6 | 10
639.1572 | 5 | 1278.3144 | 8
794.9133 | 6 | 1589.8266 | 8
882.342 | 6 | 1764.6841 | 10
935.9263 | 6 | 1871.8526 | 10
1136.2741 | 8 | 2272.5482 | 10
1332.9681 | 8 | 2665.9362 | 12
1528.3535 | 8 | 3056.707 | 12
626.346 | 5 | 1252.6919 | 8
764.9699 | 6 | 1529.9399 | 8
682.0481 | 6 | 1364.0961 | 8
802.7921 | 6 | 1605.5841 | 10
932.9167 | 6 | 1865.8335 | 10
1000.0001 | 8 | 2000.0002 | 10
753.2463 | 6 | 1506.4926 | 8
820.4429 | 6 | 1640.8858 | 10
953.3171 | 8 | 1906.6342 | 10
1029.7585 | 8 | 2059.5169 | 10
1330.3437 | 8 | 2660.6874 | 12
1378.5213 | 8 | 2757.0426 | 12
1467.9509 | 8 | 2935.9018 | 12
844.864 | 6 | 1689.7279 | 10
982.3526 | 8 | 1964.7052 | 10
1104.8611 | 8 | 2209.7222 | 10
1214.4257 | 8 | 2428.8514 | 10
1383.6857 | 8 | 2767.3715 | 12
1551.2098 | 8 | 3102.4196 | 12
1664.6746 | 10 | 3329.3491 | 12
840.7876 | 6 | 1681.5751 | 10
995.4751 | 8 | 1990.9502 | 10
1093.6698 | 8 | 2187.3397 | 10
1144.8546 | 8 | 2289.7092 | 10
1204.5001 | 8 | 2409.0002 | 10
1252.5 | 8 | 2505 | 12
648.3835 | 5 | 1296.767 | 8
820.3589 | 6 | 1640.7178 | 10
941.0352 | 6 | 1882.0704 | 10
1045.3157 | 8 | 2090.6314 | 10
1136.5096 | 8 | 2273.0192 | 10
1235.933 | 8 | 2471.866 | 10
1229.0007 | 8 | 2458.0014 | 10
1303.9328 | 8 | 2607.8655 | 12
1403.874 | 8 | 2807.748 | 12
1484.3188 | 8 | 2968.6376 | 12
1171.9065 | 8 | 2343.8131 | 10
1316.9347 | 8 | 2633.8694 | 12
1454.2378 | 8 | 2908.4756 | 12
1568.7217 | 8 | 3137.4434 | 12
1414.8836 | 8 | 2829.7672 | 12
1523.3743 | 8 | 3046.7486 | 12
1625.1171 | 10 | 3250.2342 | 12
1757.2796 | 10 | 3514.5593 | 12
1846.8509 | 10 | 3693.7017 | 14
1914.581 | 10 | 3829.162 | 14
1634.3829 | 10 | 3268.7658 | 12
1915.2738 | 10 | 3830.5476 | 14
2165.2718 | 10 | 4330.5437 | 16
1914.1469 | 10 | 3828.2938 | 14
2017.9874 | 10 | 4035.9748 | 14
2141.5995 | 10 | 4283.199 | 16
2290.5785 | 10 | 4581.157 | 16
1727.4951 | 10 | 3454.9903 | 12
1826.6982 | 10 | 3653.3965 | 14
2003.3556 | 10 | 4006.7112 | 14
2187.1986 | 10 | 4374.3972 | 16
2293.6739 | 10 | 4587.3477 | 16
2422.2984 | 10 | 4844.5968 | 16
2547.3614 | 12 | 5094.7228 | 16
2953.0528 | 12 | 5906.1056 | 18
3220.9607 | 12 | 6441.9215 | 18
3579.8797 | 14 | 7159.7593 | 20
3926.8748 | 14 | 7853.7497 | 20
4128.2784 | 14 | 8256.5567 | 20
120.9035 | 2.5 | 362.7105 | 4
134.1949 | 3 | 402.5848 | 5
146.7341 | 3 | 440.2024 | 5
154 | 3 | 462 | 5
79 | 2 | 237 | 4
169.9715 | 3 | 509.9146 | 5
191.939 | 3 | 575.8169 | 5
226.3257 | 4 | 678.977 | 6
124.0691 | 2.5 | 372.2073 | 4
190.191 | 3 | 570.5729 | 5
214.0515 | 3 | 642.1546 | 5
249.8523 | 4 | 749.5569 | 6
243.9916 | 4 | 731.9747 | 6
128.156 | 3 | 384.4681 | 4
152.95 | 3 | 458.85 | 5
168.2305 | 3 | 504.6915 | 5
184.528 | 3 | 553.584 | 5
191.32 | 3 | 573.96 | 5
90.3291 | 2.5 | 270.9873 | 4
95.22 | 2.5 | 285.66 | 4
176.1225 | 3 | 528.3676 | 5
200.368 | 3 | 601.1041 | 5
232.5586 | 4 | 697.6759 | 6
232.5586 | 4 | 697.6759 | 6
111.4482 | 2.5 | 334.3446 | 4
118.6369 | 2.5 | 355.9106 | 4
205.3636 | 3 | 616.0908 | 5
235.6474 | 4 | 706.9421 | 6
257.4 | 4 | 772.2001 | 6
277.4627 | 4 | 832.388 | 6
300 | 4 | 900 | 6
300 | 4 | 900 | 6
136.1059 | 3 | 408.3177 | 5
162.637 | 3 | 487.911 | 5
165.3271 | 3 | 495.9813 | 5
271.9533 | 4 | 815.8599 | 6
309.3395 | 4 | 928.0185 | 6
341.2848 | 4 | 1023.8543 | 8
380.858 | 4 | 1142.5741 | 8
405.1149 | 5 | 1215.3446 | 8
406.8778 | 5 | 1220.6335 | 8
154.2292 | 3 | 462.6875 | 5
205.8649 | 3 | 617.5946 | 5
227.7916 | 4 | 683.3749 | 6
294.5625 | 4 | 883.6876 | 6
355.8818 | 4 | 1067.6453 | 8
415.2757 | 5 | 1245.8272 | 8
449.14 | 5 | 1347.4201 | 8
222.9265 | 4 | 668.7796 | 6
339.6329 | 4 | 1018.8988 | 8
384.0902 | 4 | 1152.2706 | 8
424.5536 | 5 | 1273.6608 | 8
491.3603 | 5 | 1474.0808 | 8
551.7418 | 5 | 1655.2254 | 10
573.0512 | 5 | 1719.1537 | 10
179.981 | 3 | 539.9431 | 5
237.9031 | 4 | 713.7094 | 6
284.3868 | 4 | 853.1603 | 6
260.585 | 4 | 781.755 | 6
273.2839 | 4 | 819.8518 | 6
330.9972 | 4 | 992.9917 | 8
524.7552 | 5 | 1574.2657 | 8
534.9404 | 5 | 1604.8213 | 10
573.9449 | 5 | 1721.8346 | 10
599.7227 | 5 | 1799.168 | 10
512.3923 | 5 | 1537.1769 | 8
573.8168 | 5 | 1721.4503 | 10
630.1667 | 5 | 1890.5 | 10
681.695 | 6 | 2045.085 | 10
242.0702 | 4 | 726.2105 | 6
291.6367 | 4 | 874.91 | 6
290.4936 | 4 | 871.4809 | 6
350.6693 | 4 | 1052.008 | 8
375.4803 | 4 | 1126.4408 | 8
402.5638 | 5 | 1207.6913 | 8
427.3855 | 5 | 1282.1565 | 8
430.0891 | 5 | 1290.2674 | 8
453.84 | 5 | 1361.52 | 8
360.7205 | 4 | 1082.1614 | 8
391.3696 | 4 | 1174.1089 | 8
444.5377 | 5 | 1333.6131 | 8
455.5928 | 5 | 1366.7783 | 8
548.8465 | 5 | 1646.5396 | 10
628.8755 | 5 | 1886.6265 | 10
683.4996 | 6 | 2050.4988 | 10
734.2064 | 6 | 2202.6191 | 10
789.7994 | 6 | 2369.3983 | 10
360.84 | 4 | 1082.52 | 8
106.8596 | 2.5 | 320.5787 | 4
913.8143 | 6 | 2741.443 | 12
969.4037 | 8 | 2908.2111 | 12
1015.343 | 8 | 3046.0289 | 12
1051.8577 | 8 | 3155.5731 | 12
1127.0937 | 8 | 3381.2812 | 12
456.5775 | 5 | 1369.7324 | 8
508.0798 | 5 | 1524.2394 | 8
534.9443 | 5 | 1604.833 | 10
568.82 | 5 | 1706.46 | 10
885.0742 | 6 | 2655.2225 | 12
912.6252 | 6 | 2737.8756 | 12
955.0129 | 8 | 2865.0386 | 12
1024.8269 | 8 | 3074.4806 | 12
1116.5838 | 8 | 3349.7514 | 12
466.2681 | 5 | 1398.8044 | 8
509.7501 | 5 | 1529.2504 | 8
543.4703 | 5 | 1630.411 | 10
607.7455 | 5 | 1823.2366 | 10
667.9 | 6 | 2003.7 | 10
732.8 | 6 | 2198.4 | 10
774.6 | 6 | 2323.8 | 10
813.5 | 6 | 2440.5 | 10
616.3385 | 5 | 1849.0154 | 10
707.5905 | 6 | 2122.7716 | 10
786.8099 | 6 | 2360.4297 | 10
825.5 | 6 | 2476.5 | 10
756.8 | 6 | 2270.4 | 10
830.5 | 6 | 2491.5 | 10
873.3 | 6 | 2619.9 | 12
639.1572 | 5 | 1917.4715 | 10
794.9133 | 6 | 2384.7399 | 10
882.342 | 6 | 2647.0261 | 12
935.9263 | 6 | 2807.7789 | 12
1136.2741 | 8 | 3408.8222 | 12
1332.9681 | 8 | 3998.9043 | 14
1528.3535 | 8 | 4585.0605 | 16
626.346 | 5 | 1879.0379 | 10
764.9699 | 6 | 2294.9098 | 10
682.0481 | 6 | 2046.1442 | 10
802.7921 | 6 | 2408.3762 | 10
932.9167 | 6 | 2798.7502 | 12
1000.0001 | 8 | 3000.0002 | 12
753.2463 | 6 | 2259.739 | 10
820.4429 | 6 | 2461.3287 | 10
953.3171 | 8 | 2859.9513 | 12
1029.7585 | 8 | 3089.2754 | 12
1330.3437 | 8 | 3991.0312 | 14
1378.5213 | 8 | 4135.5639 | 14
1467.9509 | 8 | 4403.8528 | 16
844.864 | 6 | 2534.5919 | 12
982.3526 | 8 | 2947.0578 | 12
1104.8611 | 8 | 3314.5834 | 12
1214.4257 | 8 | 3643.277 | 14
1383.6857 | 8 | 4151.0572 | 14
1551.2098 | 8 | 4653.6293 | 16
1664.6746 | 10 | 4994.0237 | 16
840.7876 | 6 | 2522.3627 | 12
995.4751 | 8 | 2986.4252 | 12
1093.6698 | 8 | 3281.0095 | 12
1144.8546 | 8 | 3434.5638 | 12
1204.5001 | 8 | 3613.5003 | 14
1252.5 | 8 | 3757.5 | 14
648.3835 | 5 | 1945.1505 | 10
820.3589 | 6 | 2461.0767 | 10
941.0352 | 6 | 2823.1056 | 12
1045.3157 | 8 | 3135.947 | 12
1136.5096 | 8 | 3409.5287 | 12
1235.933 | 8 | 3707.799 | 14
1229.0007 | 8 | 3687.0022 | 14
1303.9328 | 8 | 3911.7983 | 14
1403.874 | 8 | 4211.6221 | 14
1484.3188 | 8 | 4452.9564 | 16
1171.9065 | 8 | 3515.7196 | 12
1316.9347 | 8 | 3950.8041 | 14
1454.2378 | 8 | 4362.7133 | 16
1568.7217 | 8 | 4706.1651 | 16
1414.8836 | 8 | 4244.6507 | 14
1523.3743 | 8 | 4570.123 | 16
1625.1171 | 10 | 4875.3512 | 16
1757.2796 | 10 | 5271.8389 | 16
1846.8509 | 10 | 5540.5526 | 16
1914.581 | 10 | 5743.743 | 18
1634.3829 | 10 | 4903.1487 | 16
1915.2738 | 10 | 5745.8213 | 18
2165.2718 | 10 | 6495.8155 | 18
1914.1469 | 10 | 5742.4408 | 18
2017.9874 | 10 | 6053.9622 | 18
2141.5995 | 10 | 6424.7985 | 18
2290.5785 | 10 | 6871.7355 | 18
1727.4951 | 10 | 5182.4854 | 16
1826.6982 | 10 | 5480.0947 | 16
2003.3556 | 10 | 6010.0669 | 18
2187.1986 | 10 | 6561.5959 | 18
2293.6739 | 10 | 6881.0216 | 18
2422.2984 | 10 | 7266.8952 | 20
2547.3614 | 12 | 7642.0842 | 20
2953.0528 | 12 | 8859.1584 | 24
3220.9607 | 12 | 9662.8822 | 24
3579.8797 | 14 | 10739.639 | 24
3926.8748 | 14 | 11780.6245 | 24
4128.2784 | 14 | 12384.8351 | 24
120.9035 | 2.5 | 483.6139 | 5
134.1949 | 3 | 536.7797 | 5
146.7341 | 3 | 586.9365 | 5
154 | 3 | 616 | 5
79 | 2 | 316 | 4
169.9715 | 3 | 679.8862 | 6
191.939 | 3 | 767.7559 | 6
226.3257 | 4 | 905.3027 | 6
124.0691 | 2.5 | 496.2764 | 5
190.191 | 3 | 760.7639 | 6
214.0515 | 3 | 856.2061 | 6
249.8523 | 4 | 999.4092 | 8
243.9916 | 4 | 975.9663 | 8
128.156 | 3 | 512.6241 | 5
152.95 | 3 | 611.8001 | 5
168.2305 | 3 | 672.9221 | 6
184.528 | 3 | 738.1121 | 6
191.32 | 3 | 765.2801 | 6
90.3291 | 2.5 | 361.3164 | 4
95.22 | 2.5 | 380.88 | 4
176.1225 | 3 | 704.4902 | 6
200.368 | 3 | 801.4722 | 6
232.5586 | 4 | 930.2345 | 6
232.5586 | 4 | 930.2345 | 6
111.4482 | 2.5 | 445.7928 | 5
118.6369 | 2.5 | 474.5474 | 5
205.3636 | 3 | 821.4543 | 6
235.6474 | 4 | 942.5895 | 6
257.4 | 4 | 1029.6001 | 8
277.4627 | 4 | 1109.8506 | 8
300 | 4 | 1200 | 8
300 | 4 | 1200 | 8
136.1059 | 3 | 544.4236 | 5
162.637 | 3 | 650.548 | 6
165.3271 | 3 | 661.3083 | 6
271.9533 | 4 | 1087.8131 | 8
309.3395 | 4 | 1237.358 | 8
341.2848 | 4 | 1365.139 | 8
380.858 | 4 | 1523.4321 | 8
405.1149 | 5 | 1620.4594 | 10
406.8778 | 5 | 1627.5113 | 10
154.2292 | 3 | 616.9167 | 5
205.8649 | 3 | 823.4595 | 6
227.7916 | 4 | 911.1665 | 6
294.5625 | 4 | 1178.2501 | 8
355.8818 | 4 | 1423.5271 | 8
415.2757 | 5 | 1661.103 | 10
449.14 | 5 | 1796.5602 | 10
222.9265 | 4 | 891.7062 | 6
339.6329 | 4 | 1358.5317 | 8
384.0902 | 4 | 1536.3608 | 8
424.5536 | 5 | 1698.2144 | 10
491.3603 | 5 | 1965.4411 | 10
551.7418 | 5 | 2206.9672 | 10
573.0512 | 5 | 2292.2049 | 10
179.981 | 3 | 719.9241 | 6
237.9031 | 4 | 951.6126 | 8
284.3868 | 4 | 1137.547 | 8
260.585 | 4 | 1042.34 | 8
273.2839 | 4 | 1093.1357 | 8
330.9972 | 4 | 1323.9889 | 8
524.7552 | 5 | 2099.021 | 10
534.9404 | 5 | 2139.7617 | 10
573.9449 | 5 | 2295.7795 | 10
599.7227 | 5 | 2398.8907 | 10
512.3923 | 5 | 2049.5692 | 10
573.8168 | 5 | 2295.2671 | 10
630.1667 | 5 | 2520.6667 | 12
681.695 | 6 | 2726.78 | 12
242.0702 | 4 | 968.2806 | 8
291.6367 | 4 | 1166.5466 | 8
290.4936 | 4 | 1161.9746 | 8
350.6693 | 4 | 1402.6774 | 8
375.4803 | 4 | 1501.921 | 8
402.5638 | 5 | 1610.2551 | 10
427.3855 | 5 | 1709.542 | 10
430.0891 | 5 | 1720.3565 | 10
453.84 | 5 | 1815.36 | 10
360.7205 | 4 | 1442.8819 | 8
391.3696 | 4 | 1565.4785 | 8
444.5377 | 5 | 1778.1508 | 10
455.5928 | 5 | 1822.371 | 10
548.8465 | 5 | 2195.3862 | 10
628.8755 | 5 | 2515.502 | 12
683.4996 | 6 | 2733.9985 | 12
734.2064 | 6 | 2936.8255 | 12
789.7994 | 6 | 3159.1977 | 12
360.84 | 4 | 1443.36 | 8
106.8596 | 2.5 | 427.4383 | 5
913.8143 | 6 | 3655.2573 | 14
969.4037 | 8 | 3877.6149 | 14
1015.343 | 8 | 4061.3719 | 14
1051.8577 | 8 | 4207.4307 | 14
1127.0937 | 8 | 4508.3749 | 16
456.5775 | 5 | 1826.3098 | 10
508.0798 | 5 | 2032.3192 | 10
534.9443 | 5 | 2139.7774 | 10
568.82 | 5 | 2275.28 | 10
885.0742 | 6 | 3540.2967 | 12
912.6252 | 6 | 3650.5009 | 14
955.0129 | 8 | 3820.0514 | 14
1024.8269 | 8 | 4099.3075 | 14
1116.5838 | 8 | 4466.3352 | 16
466.2681 | 5 | 1865.0725 | 10
509.7501 | 5 | 2039.0006 | 10
543.4703 | 5 | 2173.8813 | 10
607.7455 | 5 | 2430.9822 | 10
667.9 | 6 | 2671.6 | 12
732.8 | 6 | 2931.2 | 12
774.6 | 6 | 3098.4 | 12
813.5 | 6 | 3254 | 12
616.3385 | 5 | 2465.3539 | 10
707.5905 | 6 | 2830.3621 | 12
786.8099 | 6 | 3147.2397 | 12
825.5 | 6 | 3302 | 12
756.8 | 6 | 3027.2 | 12
830.5 | 6 | 3322 | 12
873.3 | 6 | 3493.2 | 12
639.1572 | 5 | 2556.6287 | 12
794.9133 | 6 | 3179.6532 | 12
882.342 | 6 | 3529.3682 | 12
935.9263 | 6 | 3743.7052 | 14
1136.2741 | 8 | 4545.0963 | 16
1332.9681 | 8 | 5331.8724 | 16
1528.3535 | 8 | 6113.414 | 18
626.346 | 5 | 2505.3838 | 12
764.9699 | 6 | 3059.8797 | 12
682.0481 | 6 | 2728.1922 | 12
802.7921 | 6 | 3211.1683 | 12
932.9167 | 6 | 3731.667 | 14
1000.0001 | 8 | 4000.0003 | 14
753.2463 | 6 | 3012.9853 | 12
820.4429 | 6 | 3281.7717 | 12
953.3171 | 8 | 3813.2684 | 14
1029.7585 | 8 | 4119.0339 | 14
1330.3437 | 8 | 5321.3749 | 16
1378.5213 | 8 | 5514.0852 | 16
1467.9509 | 8 | 5871.8037 | 18
844.864 | 6 | 3379.4558 | 12
982.3526 | 8 | 3929.4104 | 14
1104.8611 | 8 | 4419.4445 | 16
1214.4257 | 8 | 4857.7027 | 16
1383.6857 | 8 | 5534.743 | 16
1551.2098 | 8 | 6204.8391 | 18
1664.6746 | 10 | 6658.6983 | 18
840.7876 | 6 | 3363.1503 | 12
995.4751 | 8 | 3981.9003 | 14
1093.6698 | 8 | 4374.6794 | 16
1144.8546 | 8 | 4579.4184 | 16
1204.5001 | 8 | 4818.0004 | 16
1252.5 | 8 | 5010 | 16
648.3835 | 5 | 2593.534 | 12
820.3589 | 6 | 3281.4355 | 12
941.0352 | 6 | 3764.1408 | 14
1045.3157 | 8 | 4181.2627 | 14
1136.5096 | 8 | 4546.0383 | 16
1235.933 | 8 | 4943.7321 | 16
1229.0007 | 8 | 4916.0029 | 16
1303.9328 | 8 | 5215.731 | 16
1403.874 | 8 | 5615.4961 | 18
1484.3188 | 8 | 5937.2753 | 18
1171.9065 | 8 | 4687.6261 | 16
1316.9347 | 8 | 5267.7388 | 16
1454.2378 | 8 | 5816.9511 | 18
1568.7217 | 8 | 6274.8868 | 18
1414.8836 | 8 | 5659.5343 | 18
1523.3743 | 8 | 6093.4973 | 18
1625.1171 | 10 | 6500.4683 | 18
1757.2796 | 10 | 7029.1185 | 18
1846.8509 | 10 | 7387.4035 | 20
1914.581 | 10 | 7658.324 | 20
1634.3829 | 10 | 6537.5317 | 18
1915.2738 | 10 | 7661.0951 | 20
2165.2718 | 10 | 8661.0874 | 20
1914.1469 | 10 | 7656.5877 | 20
2017.9874 | 10 | 8071.9496 | 20
2141.5995 | 10 | 8566.398 | 20
2290.5785 | 10 | 9162.314 | 24
1727.4951 | 10 | 6909.9805 | 18
1826.6982 | 10 | 7306.7929 | 20
2003.3556 | 10 | 8013.4225 | 20
2187.1986 | 10 | 8748.7945 | 20
2293.6739 | 10 | 9174.6955 | 24
2422.2984 | 10 | 9689.1937 | 24
2547.3614 | 12 | 10189.4456 | 24
2953.0528 | 12 | 11812.2111 | 24
3220.9607 | 12 | 12883.8429 | 24
3579.8797 | 14 | 14319.5187 | 24
3926.8748 | 14 | 15707.4993 | 24
4128.2784 | 14 | 16513.1135 | 24
120.9035 | 2.5 | 120.9035 | 2.5
134.1949 | 3 | 134.1949 | 3
146.7341 | 3 | 146.7341 | 3
154 | 3 | 154 | 3
79 | 2 | 79 | 2
169.9715 | 3 | 169.9715 | 3
191.939 | 3 | 191.939 | 3
226.3257 | 4 | 226.3257 | 4
124.0691 | 2.5 | 124.0691 | 2.5
190.191 | 3 | 190.191 | 3
214.0515 | 3 | 214.0515 | 3
249.8523 | 4 | 249.8523 | 4
243.9916 | 4 | 243.9916 | 4
128.156 | 3 | 128.156 | 3
152.95 | 3 | 152.95 | 3
168.2305 | 3 | 168.2305 | 3
184.528 | 3 | 184.528 | 3
191.32 | 3 | 191.32 | 3
90.3291 | 2.5 | 90.3291 | 2.5
95.22 | 2.5 | 95.22 | 2.5
176.1225 | 3 | 176.1225 | 3
200.368 | 3 | 200.368 | 3
232.5586 | 4 | 232.5586 | 4
232.5586 | 4 | 232.5586 | 4
111.4482 | 2.5 | 111.4482 | 2.5
118.6369 | 2.5 | 118.6369 | 2.5
205.3636 | 3 | 205.3636 | 3
235.6474 | 4 | 235.6474 | 4
257.4 | 4 | 257.4 | 4
277.4627 | 4 | 277.4627 | 4
300 | 4 | 300 | 4
300 | 4 | 300 | 4
136.1059 | 3 | 136.1059 | 3
162.637 | 3 | 162.637 | 3
165.3271 | 3 | 165.3271 | 3
271.9533 | 4 | 271.9533 | 4
309.3395 | 4 | 309.3395 | 4
341.2848 | 4 | 341.2848 | 4
380.858 | 4 | 380.858 | 4
405.1149 | 5 | 405.1149 | 5
406.8778 | 5 | 406.8778 | 5
154.2292 | 3 | 154.2292 | 3
205.8649 | 3 | 205.8649 | 3
227.7916 | 4 | 227.7916 | 4
294.5625 | 4 | 294.5625 | 4
355.8818 | 4 | 355.8818 | 4
415.2757 | 5 | 415.2757 | 5
449.14 | 5 | 449.14 | 5
222.9265 | 4 | 222.9265 | 4
339.6329 | 4 | 339.6329 | 4
384.0902 | 4 | 384.0902 | 4
424.5536 | 5 | 424.5536 | 5
491.3603 | 5 | 491.3603 | 5
551.7418 | 5 | 551.7418 | 5
573.0512 | 5 | 573.0512 | 5
179.981 | 3 | 179.981 | 3
237.9031 | 4 | 237.9031 | 4
284.3868 | 4 | 284.3868 | 4
260.585 | 4 | 260.585 | 4
273.2839 | 4 | 273.2839 | 4
330.9972 | 4 | 330.9972 | 4
524.7552 | 5 | 524.7552 | 5
534.9404 | 5 | 534.9404 | 5
573.9449 | 5 | 573.9449 | 5
599.7227 | 5 | 599.7227 | 5
512.3923 | 5 | 512.3923 | 5
573.8168 | 5 | 573.8168 | 5
630.1667 | 5 | 630.1667 | 5
681.695 | 6 | 681.695 | 6
242.0702 | 4 | 242.0702 | 4
291.6367 | 4 | 291.6367 | 4
290.4936 | 4 | 290.4936 | 4
350.6693 | 4 | 350.6693 | 4
375.4803 | 4 | 375.4803 | 4
402.5638 | 5 | 402.5638 | 5
427.3855 | 5 | 427.3855 | 5
430.0891 | 5 | 430.0891 | 5
453.84 | 5 | 453.84 | 5
360.7205 | 4 | 360.7205 | 4
391.3696 | 4 | 391.3696 | 4
444.5377 | 5 | 444.5377 | 5
455.5928 | 5 | 455.5928 | 5
548.8465 | 5 | 548.8465 | 5
628.8755 | 5 | 628.8755 | 5
683.4996 | 6 | 683.4996 | 6
734.2064 | 6 | 734.2064 | 6
789.7994 | 6 | 789.7994 | 6
360.84 | 4 | 360.84 | 4
106.8596 | 2.5 | 106.8596 | 2.5
913.8143 | 6 | 913.8143 | 6
969.4037 | 8 | 969.4037 | 8
1015.343 | 8 | 1015.343 | 8
1051.8577 | 8 | 1051.8577 | 8
1127.0937 | 8 | 1127.0937 | 8
456.5775 | 5 | 456.5775 | 5
508.0798 | 5 | 508.0798 | 5
534.9443 | 5 | 534.9443 | 5
568.82 | 5 | 568.82 | 5
885.0742 | 6 | 885.0742 | 6
912.6252 | 6 | 912.6252 | 6
955.0129 | 8 | 955.0129 | 8
1024.8269 | 8 | 1024.8269 | 8
1116.5838 | 8 | 1116.5838 | 8
466.2681 | 5 | 466.2681 | 5
509.7501 | 5 | 509.7501 | 5
543.4703 | 5 | 543.4703 | 5
607.7455 | 5 | 607.7455 | 5
667.9 | 6 | 667.9 | 6
732.8 | 6 | 732.8 | 6
774.6 | 6 | 774.6 | 6
813.5 | 6 | 813.5 | 6
616.3385 | 5 | 616.3385 | 5
707.5905 | 6 | 707.5905 | 6
786.8099 | 6 | 786.8099 | 6
825.5 | 6 | 825.5 | 6
756.8 | 6 | 756.8 | 6
830.5 | 6 | 830.5 | 6
873.3 | 6 | 873.3 | 6
639.1572 | 5 | 639.1572 | 5
794.9133 | 6 | 794.9133 | 6
882.342 | 6 | 882.342 | 6
935.9263 | 6 | 935.9263 | 6
1136.2741 | 8 | 1136.2741 | 8
1332.9681 | 8 | 1332.9681 | 8
1528.3535 | 8 | 1528.3535 | 8
626.346 | 5 | 626.346 | 5
764.9699 | 6 | 764.9699 | 6
682.0481 | 6 | 682.0481 | 6
802.7921 | 6 | 802.7921 | 6
932.9167 | 6 | 932.9167 | 6
1000.0001 | 8 | 1000.0001 | 8
753.2463 | 6 | 753.2463 | 6
820.4429 | 6 | 820.4429 | 6
953.3171 | 8 | 953.3171 | 8
1029.7585 | 8 | 1029.7585 | 8
1330.3437 | 8 | 1330.3437 | 8
1378.5213 | 8 | 1378.5213 | 8
1467.9509 | 8 | 1467.9509 | 8
844.864 | 6 | 844.864 | 6
982.3526 | 8 | 982.3526 | 8
1104.8611 | 8 | 1104.8611 | 8
1214.4257 | 8 | 1214.4257 | 8
1383.6857 | 8 | 1383.6857 | 8
1551.2098 | 8 | 1551.2098 | 8
1664.6746 | 10 | 1664.6746 | 10
840.7876 | 6 | 840.7876 | 6
995.4751 | 8 | 995.4751 | 8
1093.6698 | 8 | 1093.6698 | 8
1144.8546 | 8 | 1144.8546 | 8
1204.5001 | 8 | 1204.5001 | 8
1252.5 | 8 | 1252.5 | 8
648.3835 | 5 | 648.3835 | 5
820.3589 | 6 | 820.3589 | 6
941.0352 | 6 | 941.0352 | 6
1045.3157 | 8 | 1045.3157 | 8
1136.5096 | 8 | 1136.5096 | 8
1235.933 | 8 | 1235.933 | 8
1229.0007 | 8 | 1229.0007 | 8
1303.9328 | 8 | 1303.9328 | 8
1403.874 | 8 | 1403.874 | 8
1484.3188 | 8 | 1484.3188 | 8
1171.9065 | 8 | 1171.9065 | 8
1316.9347 | 8 | 1316.9347 | 8
1454.2378 | 8 | 1454.2378 | 8
1568.7217 | 8 | 1568.7217 | 8
1414.8836 | 8 | 1414.8836 | 8
1523.3743 | 8 | 1523.3743 | 8
1625.1171 | 10 | 1625.1171 | 10
1757.2796 | 10 | 1757.2796 | 10
1846.8509 | 10 | 1846.8509 | 10
1914.581 | 10 | 1914.581 | 10
1634.3829 | 10 | 1634.3829 | 10
1915.2738 | 10 | 1915.2738 | 10
2165.2718 | 10 | 2165.2718 | 10
1914.1469 | 10 | 1914.1469 | 10
2017.9874 | 10 | 2017.9874 | 10
2141.5995 | 10 | 2141.5995 | 10
2290.5785 | 10 | 2290.5785 | 10
1727.4951 | 10 | 1727.4951 | 10
1826.6982 | 10 | 1826.6982 | 10
2003.3556 | 10 | 2003.3556 | 10
2187.1986 | 10 | 2187.1986 | 10
2293.6739 | 10 | 2293.6739 | 10
2422.2984 | 10 | 2422.2984 | 10
2547.3614 | 12 | 2547.3614 | 12
2953.0528 | 12 | 2953.0528 | 12
3220.9607 | 12 | 3220.9607 | 12
3579.8797 | 14 | 3579.8797 | 14
3926.8748 | 14 | 3926.8748 | 14
4128.2784 | 14 | 4128.2784 | 14
120.9035 | 2.5 | 241.807 | 4
134.1949 | 3 | 268.3898 | 4
146.7341 | 3 | 293.4682 | 4
154 | 3 | 308 | 4
79 | 2 | 158 | 3
169.9715 | 3 | 339.9431 | 4
191.939 | 3 | 383.8779 | 4
226.3257 | 4 | 452.6514 | 5
124.0691 | 2.5 | 248.1382 | 4
190.191 | 3 | 380.3819 | 4
214.0515 | 3 | 428.1031 | 5
249.8523 | 4 | 499.7046 | 5
243.9916 | 4 | 487.9832 | 5
128.156 | 3 | 256.3121 | 4
152.95 | 3 | 305.9 | 4
168.2305 | 3 | 336.461 | 4
184.528 | 3 | 369.056 | 4
191.32 | 3 | 382.64 | 4
90.3291 | 2.5 | 180.6582 | 3
95.22 | 2.5 | 190.44 | 3
176.1225 | 3 | 352.2451 | 4
200.368 | 3 | 400.7361 | 5
232.5586 | 4 | 465.1173 | 5
232.5586 | 4 | 465.1173 | 5
111.4482 | 2.5 | 222.8964 | 4
118.6369 | 2.5 | 237.2737 | 4
205.3636 | 3 | 410.7272 | 5
235.6474 | 4 | 471.2947 | 5
257.4 | 4 | 514.8 | 5
277.4627 | 4 | 554.9253 | 5
300 | 4 | 600 | 5
300 | 4 | 600 | 5
136.1059 | 3 | 272.2118 | 4
162.637 | 3 | 325.274 | 4
165.3271 | 3 | 330.6542 | 4
271.9533 | 4 | 543.9066 | 5
309.3395 | 4 | 618.679 | 5
341.2848 | 4 | 682.5695 | 6
380.858 | 4 | 761.716 | 6
405.1149 | 5 | 810.2297 | 6
406.8778 | 5 | 813.7556 | 6
154.2292 | 3 | 308.4583 | 4
205.8649 | 3 | 411.7298 | 5
227.7916 | 4 | 455.5833 | 5
294.5625 | 4 | 589.1251 | 5
355.8818 | 4 | 711.7636 | 6
415.2757 | 5 | 830.5515 | 6
449.14 | 5 | 898.2801 | 6
222.9265 | 4 | 445.8531 | 5
339.6329 | 4 | 679.2659 | 6
384.0902 | 4 | 768.1804 | 6
424.5536 | 5 | 849.1072 | 6
491.3603 | 5 | 982.7205 | 8
551.7418 | 5 | 1103.4836 | 8
573.0512 | 5 | 1146.1024 | 8
179.981 | 3 | 359.9621 | 4
237.9031 | 4 | 475.8063 | 5
284.3868 | 4 | 568.7735 | 5
260.585 | 4 | 521.17 | 5
273.2839 | 4 | 546.5679 | 5
330.9972 | 4 | 661.9944 | 6
524.7552 | 5 | 1049.5105 | 8
534.9404 | 5 | 1069.8809 | 8
573.9449 | 5 | 1147.8898 | 8
599.7227 | 5 | 1199.4453 | 8
512.3923 | 5 | 1024.7846 | 8
573.8168 | 5 | 1147.6336 | 8
630.1667 | 5 | 1260.3334 | 8
681.695 | 6 | 1363.39 | 8
242.0702 | 4 | 484.1403 | 5
291.6367 | 4 | 583.2733 | 5
290.4936 | 4 | 580.9873 | 5
350.6693 | 4 | 701.3387 | 6
375.4803 | 4 | 750.9605 | 6
402.5638 | 5 | 805.1276 | 6
427.3855 | 5 | 854.771 | 6
430.0891 | 5 | 860.1783 | 6
453.84 | 5 | 907.68 | 6
360.7205 | 4 | 721.4409 | 6
391.3696 | 4 | 782.7393 | 6
444.5377 | 5 | 889.0754 | 6
455.5928 | 5 | 911.1855 | 6
548.8465 | 5 | 1097.6931 | 8
628.8755 | 5 | 1257.751 | 8
683.4996 | 6 | 1366.9992 | 8
734.2064 | 6 | 1468.4128 | 8
789.7994 | 6 | 1579.5988 | 8
360.84 | 4 | 721.68 | 6
106.8596 | 2.5 | 213.7192 | 3
913.8143 | 6 | 1827.6287 | 10
969.4037 | 8 | 1938.8074 | 10
1015.343 | 8 | 2030.6859 | 10
1051.8577 | 8 | 2103.7154 | 10
1127.0937 | 8 | 2254.1875 | 10
456.5775 | 5 | 913.1549 | 6
508.0798 | 5 | 1016.1596 | 8
534.9443 | 5 | 1069.8887 | 8
568.82 | 5 | 1137.64 | 8
885.0742 | 6 | 1770.1484 | 10
912.6252 | 6 | 1825.2504 | 10
955.0129 | 8 | 1910.0257 | 10
1024.8269 | 8 | 2049.6538 | 10
1116.5838 | 8 | 2233.1676 | 10
466.2681 | 5 | 932.5363 | 6
509.7501 | 5 | 1019.5003 | 8
543.4703 | 5 | 1086.9406 | 8
607.7455 | 5 | 1215.4911 | 8
667.9 | 6 | 1335.8 | 8
732.8 | 6 | 1465.6 | 8
774.6 | 6 | 1549.2 | 8
813.5 | 6 | 1627 | 10
616.3385 | 5 | 1232.6769 | 8
707.5905 | 6 | 1415.1811 | 8
786.8099 | 6 | 1573.6198 | 8
825.5 | 6 | 1651 | 10
756.8 | 6 | 1513.6 | 8
830.5 | 6 | 1661 | 10
873.3 | 6 | 1746.6 | 10
639.1572 | 5 | 1278.3144 | 8
794.9133 | 6 | 1589.8266 | 8
882.342 | 6 | 1764.6841 | 10
935.9263 | 6 | 1871.8526 | 10
1136.2741 | 8 | 2272.5482 | 10
1332.9681 | 8 | 2665.9362 | 12
1528.3535 | 8 | 3056.707 | 12
626.346 | 5 | 1252.6919 | 8
764.9699 | 6 | 1529.9399 | 8
682.0481 | 6 | 1364.0961 | 8
802.7921 | 6 | 1605.5841 | 10
932.9167 | 6 | 1865.8335 | 10
1000.0001 | 8 | 2000.0002 | 10
753.2463 | 6 | 1506.4926 | 8
820.4429 | 6 | 1640.8858 | 10
953.3171 | 8 | 1906.6342 | 10
1029.7585 | 8 | 2059.5169 | 10
1330.3437 | 8 | 2660.6874 | 12
1378.5213 | 8 | 2757.0426 | 12
1467.9509 | 8 | 2935.9018 | 12
844.864 | 6 | 1689.7279 | 10
982.3526 | 8 | 1964.7052 | 10
1104.8611 | 8 | 2209.7222 | 10
1214.4257 | 8 | 2428.8514 | 10
1383.6857 | 8 | 2767.3715 | 12
1551.2098 | 8 | 3102.4196 | 12
1664.6746 | 10 | 3329.3491 | 12
840.7876 | 6 | 1681.5751 | 10
995.4751 | 8 | 1990.9502 | 10
1093.6698 | 8 | 2187.3397 | 10
1144.8546 | 8 | 2289.7092 | 10
1204.5001 | 8 | 2409.0002 | 10
1252.5 | 8 | 2505 | 12
648.3835 | 5 | 1296.767 | 8
820.3589 | 6 | 1640.7178 | 10
941.0352 | 6 | 1882.0704 | 10
1045.3157 | 8 | 2090.6314 | 10
1136.5096 | 8 | 2273.0192 | 10
1235.933 | 8 | 2471.866 | 10
1229.0007 | 8 | 2458.0014 | 10
1303.9328 | 8 | 2607.8655 | 12
1403.874 | 8 | 2807.748 | 12
1484.3188 | 8 | 2968.6376 | 12
1171.9065 | 8 | 2343.8131 | 10
1316.9347 | 8 | 2633.8694 | 12
1454.2378 | 8 | 2908.4756 | 12
1568.7217 | 8 | 3137.4434 | 12
1414.8836 | 8 | 2829.7672 | 12
1523.3743 | 8 | 3046.7486 | 12
1625.1171 | 10 | 3250.2342 | 12
1757.2796 | 10 | 3514.5593 | 12
1846.8509 | 10 | 3693.7017 | 14
1914.581 | 10 | 3829.162 | 14
1634.3829 | 10 | 3268.7658 | 12
1915.2738 | 10 | 3830.5476 | 14
2165.2718 | 10 | 4330.5437 | 16
1914.1469 | 10 | 3828.2938 | 14
2017.9874 | 10 | 4035.9748 | 14
2141.5995 | 10 | 4283.199 | 16
2290.5785 | 10 | 4581.157 | 16
1727.4951 | 10 | 3454.9903 | 12
1826.6982 | 10 | 3653.3965 | 14
2003.3556 | 10 | 4006.7112 | 14
2187.1986 | 10 | 4374.3972 | 16
2293.6739 | 10 | 4587.3477 | 16
2422.2984 | 10 | 4844.5968 | 16
2547.3614 | 12 | 5094.7228 | 16
2953.0528 | 12 | 5906.1056 | 18
3220.9607 | 12 | 6441.9215 | 18
3579.8797 | 14 | 7159.7593 | 20
3926.8748 | 14 | 7853.7497 | 20
4128.2784 | 14 | 8256.5567 | 20
120.9035 | 2.5 | 362.7105 | 4
134.1949 | 3 | 402.5848 | 5
146.7341 | 3 | 440.2024 | 5
154 | 3 | 462 | 5
79 | 2 | 237 | 4
169.9715 | 3 | 509.9146 | 5
191.939 | 3 | 575.8169 | 5
226.3257 | 4 | 678.977 | 6
124.0691 | 2.5 | 372.2073 | 4
190.191 | 3 | 570.5729 | 5
214.0515 | 3 | 642.1546 | 5
249.8523 | 4 | 749.5569 | 6
243.9916 | 4 | 731.9747 | 6
128.156 | 3 | 384.4681 | 4
152.95 | 3 | 458.85 | 5
168.2305 | 3 | 504.6915 | 5
184.528 | 3 | 553.584 | 5
191.32 | 3 | 573.96 | 5
90.3291 | 2.5 | 270.9873 | 4
95.22 | 2.5 | 285.66 | 4
176.1225 | 3 | 528.3676 | 5
200.368 | 3 | 601.1041 | 5
232.5586 | 4 | 697.6759 | 6
232.5586 | 4 | 697.6759 | 6
111.4482 | 2.5 | 334.3446 | 4
118.6369 | 2.5 | 355.9106 | 4
205.3636 | 3 | 616.0908 | 5
235.6474 | 4 | 706.9421 | 6
257.4 | 4 | 772.2001 | 6
277.4627 | 4 | 832.388 | 6
300 | 4 | 900 | 6
300 | 4 | 900 | 6
136.1059 | 3 | 408.3177 | 5
162.637 | 3 | 487.911 | 5
165.3271 | 3 | 495.9813 | 5
271.9533 | 4 | 815.8599 | 6
309.3395 | 4 | 928.0185 | 6
341.2848 | 4 | 1023.8543 | 8
380.858 | 4 | 1142.5741 | 8
405.1149 | 5 | 1215.3446 | 8
406.8778 | 5 | 1220.6335 | 8
154.2292 | 3 | 462.6875 | 5
205.8649 | 3 | 617.5946 | 5
227.7916 | 4 | 683.3749 | 6
294.5625 | 4 | 883.6876 | 6
355.8818 | 4 | 1067.6453 | 8
415.2757 | 5 | 1245.8272 | 8
449.14 | 5 | 1347.4201 | 8
222.9265 | 4 | 668.7796 | 6
339.6329 | 4 | 1018.8988 | 8
384.0902 | 4 | 1152.2706 | 8
424.5536 | 5 | 1273.6608 | 8
491.3603 | 5 | 1474.0808 | 8
551.7418 | 5 | 1655.2254 | 10
573.0512 | 5 | 1719.1537 | 10
179.981 | 3 | 539.9431 | 5
237.9031 | 4 | 713.7094 | 6
284.3868 | 4 | 853.1603 | 6
260.585 | 4 | 781.755 | 6
273.2839 | 4 | 819.8518 | 6
330.9972 | 4 | 992.9917 | 8
524.7552 | 5 | 1574.2657 | 8
534.9404 | 5 | 1604.8213 | 10
573.9449 | 5 | 1721.8346 | 10
599.7227 | 5 | 1799.168 | 10
512.3923 | 5 | 1537.1769 | 8
573.8168 | 5 | 1721.4503 | 10
630.1667 | 5 | 1890.5 | 10
681.695 | 6 | 2045.085 | 10
242.0702 | 4 | 726.2105 | 6
291.6367 | 4 | 874.91 | 6
290.4936 | 4 | 871.4809 | 6
350.6693 | 4 | 1052.008 | 8
375.4803 | 4 | 1126.4408 | 8
402.5638 | 5 | 1207.6913 | 8
427.3855 | 5 | 1282.1565 | 8
430.0891 | 5 | 1290.2674 | 8
453.84 | 5 | 1361.52 | 8
360.7205 | 4 | 1082.1614 | 8
391.3696 | 4 | 1174.1089 | 8
444.5377 | 5 | 1333.6131 | 8
455.5928 | 5 | 1366.7783 | 8
548.8465 | 5 | 1646.5396 | 10
628.8755 | 5 | 1886.6265 | 10
683.4996 | 6 | 2050.4988 | 10
734.2064 | 6 | 2202.6191 | 10
789.7994 | 6 | 2369.3983 | 10
360.84 | 4 | 1082.52 | 8
106.8596 | 2.5 | 320.5787 | 4
913.8143 | 6 | 2741.443 | 12
969.4037 | 8 | 2908.2111 | 12
1015.343 | 8 | 3046.0289 | 12
1051.8577 | 8 | 3155.5731 | 12
1127.0937 | 8 | 3381.2812 | 12
456.5775 | 5 | 1369.7324 | 8
508.0798 | 5 | 1524.2394 | 8
534.9443 | 5 | 1604.833 | 10
568.82 | 5 | 1706.46 | 10
885.0742 | 6 | 2655.2225 | 12
912.6252 | 6 | 2737.8756 | 12
955.0129 | 8 | 2865.0386 | 12
1024.8269 | 8 | 3074.4806 | 12
1116.5838 | 8 | 3349.7514 | 12
466.2681 | 5 | 1398.8044 | 8
509.7501 | 5 | 1529.2504 | 8
543.4703 | 5 | 1630.411 | 10
607.7455 | 5 | 1823.2366 | 10
667.9 | 6 | 2003.7 | 10
732.8 | 6 | 2198.4 | 10
774.6 | 6 | 2323.8 | 10
813.5 | 6 | 2440.5 | 10
616.3385 | 5 | 1849.0154 | 10
707.5905 | 6 | 2122.7716 | 10
786.8099 | 6 | 2360.4297 | 10
825.5 | 6 | 2476.5 | 10
756.8 | 6 | 2270.4 | 10
830.5 | 6 | 2491.5 | 10
873.3 | 6 | 2619.9 | 12
639.1572 | 5 | 1917.4715 | 10
794.9133 | 6 | 2384.7399 | 10
882.342 | 6 | 2647.0261 | 12
935.9263 | 6 | 2807.7789 | 12
1136.2741 | 8 | 3408.8222 | 12
1332.9681 | 8 | 3998.9043 | 14
1528.3535 | 8 | 4585.0605 | 16
626.346 | 5 | 1879.0379 | 10
764.9699 | 6 | 2294.9098 | 10
682.0481 | 6 | 2046.1442 | 10
802.7921 | 6 | 2408.3762 | 10
932.9167 | 6 | 2798.7502 | 12
1000.0001 | 8 | 3000.0002 | 12
753.2463 | 6 | 2259.739 | 10
820.4429 | 6 | 2461.3287 | 10
953.3171 | 8 | 2859.9513 | 12
1029.7585 | 8 | 3089.2754 | 12
1330.3437 | 8 | 3991.0312 | 14
1378.5213 | 8 | 4135.5639 | 14
1467.9509 | 8 | 4403.8528 | 16
844.864 | 6 | 2534.5919 | 12
982.3526 | 8 | 2947.0578 | 12
1104.8611 | 8 | 3314.5834 | 12
1214.4257 | 8 | 3643.277 | 14
1383.6857 | 8 | 4151.0572 | 14
1551.2098 | 8 | 4653.6293 | 16
1664.6746 | 10 | 4994.0237 | 16
840.7876 | 6 | 2522.3627 | 12
995.4751 | 8 | 2986.4252 | 12
1093.6698 | 8 | 3281.0095 | 12
1144.8546 | 8 | 3434.5638 | 12
1204.5001 | 8 | 3613.5003 | 14
1252.5 | 8 | 3757.5 | 14
648.3835 | 5 | 1945.1505 | 10
820.3589 | 6 | 2461.0767 | 10
941.0352 | 6 | 2823.1056 | 12
1045.3157 | 8 | 3135.947 | 12
1136.5096 | 8 | 3409.5287 | 12
1235.933 | 8 | 3707.799 | 14
1229.0007 | 8 | 3687.0022 | 14
1303.9328 | 8 | 3911.7983 | 14
1403.874 | 8 | 4211.6221 | 14
1484.3188 | 8 | 4452.9564 | 16
1171.9065 | 8 | 3515.7196 | 12
1316.9347 | 8 | 3950.8041 | 14
1454.2378 | 8 | 4362.7133 | 16
1568.7217 | 8 | 4706.1651 | 16
1414.8836 | 8 | 4244.6507 | 14
1523.3743 | 8 | 4570.123 | 16
1625.1171 | 10 | 4875.3512 | 16
1757.2796 | 10 | 5271.8389 | 16
1846.8509 | 10 | 5540.5526 | 16
1914.581 | 10 | 5743.743 | 18
1634.3829 | 10 | 4903.1487 | 16
1915.2738 | 10 | 5745.8213 | 18
2165.2718 | 10 | 6495.8155 | 18
1914.1469 | 10 | 5742.4408 | 18
2017.9874 | 10 | 6053.9622 | 18
2141.5995 | 10 | 6424.7985 | 18
2290.5785 | 10 | 6871.7355 | 18
1727.4951 | 10 | 5182.4854 | 16
1826.6982 | 10 | 5480.0947 | 16
2003.3556 | 10 | 6010.0669 | 18
2187.1986 | 10 | 6561.5959 | 18
2293.6739 | 10 | 6881.0216 | 18
2422.2984 | 10 | 7266.8952 | 20
2547.3614 | 12 | 7642.0842 | 20
2953.0528 | 12 | 8859.1584 | 24
3220.9607 | 12 | 9662.8822 | 24
3579.8797 | 14 | 10739.639 | 24
3926.8748 | 14 | 11780.6245 | 24
4128.2784 | 14 | 12384.8351 | 24
120.9035 | 2.5 | 241.807 | 4
134.1949 | 3 | 268.3898 | 4
146.7341 | 3 | 293.4682 | 4
154 | 3 | 308 | 4
79 | 2 | 158 | 3
169.9715 | 3 | 339.9431 | 4
191.939 | 3 | 383.8779 | 4
226.3257 | 4 | 452.6514 | 5
124.0691 | 2.5 | 248.1382 | 4
190.191 | 3 | 380.3819 | 4
214.0515 | 3 | 428.1031 | 5
249.8523 | 4 | 499.7046 | 5
243.9916 | 4 | 487.9832 | 5
128.156 | 3 | 256.3121 | 4
152.95 | 3 | 305.9 | 4
168.2305 | 3 | 336.461 | 4
184.528 | 3 | 369.056 | 4
191.32 | 3 | 382.64 | 4
90.3291 | 2.5 | 180.6582 | 3
95.22 | 2.5 | 190.44 | 3
176.1225 | 3 | 352.2451 | 4
200.368 | 3 | 400.7361 | 5
232.5586 | 4 | 465.1173 | 5
232.5586 | 4 | 465.1173 | 5
111.4482 | 2.5 | 222.8964 | 4
118.6369 | 2.5 | 237.2737 | 4
205.3636 | 3 | 410.7272 | 5
235.6474 | 4 | 471.2947 | 5
257.4 | 4 | 514.8 | 5
277.4627 | 4 | 554.9253 | 5
300 | 4 | 600 | 5
300 | 4 | 600 | 5
136.1059 | 3 | 272.2118 | 4
162.637 | 3 | 325.274 | 4
165.3271 | 3 | 330.6542 | 4
271.9533 | 4 | 543.9066 | 5
309.3395 | 4 | 618.679 | 5
341.2848 | 4 | 682.5695 | 6
380.858 | 4 | 761.716 | 6
405.1149 | 5 | 810.2297 | 6
406.8778 | 5 | 813.7556 | 6
154.2292 | 3 | 308.4583 | 4
205.8649 | 3 | 411.7298 | 5
227.7916 | 4 | 455.5833 | 5
294.5625 | 4 | 589.1251 | 5
355.8818 | 4 | 711.7636 | 6
415.2757 | 5 | 830.5515 | 6
449.14 | 5 | 898.2801 | 6
222.9265 | 4 | 445.8531 | 5
339.6329 | 4 | 679.2659 | 6
384.0902 | 4 | 768.1804 | 6
424.5536 | 5 | 849.1072 | 6
491.3603 | 5 | 982.7205 | 8
551.7418 | 5 | 1103.4836 | 8
573.0512 | 5 | 1146.1024 | 8
179.981 | 3 | 359.9621 | 4
237.9031 | 4 | 475.8063 | 5
284.3868 | 4 | 568.7735 | 5
260.585 | 4 | 521.17 | 5
273.2839 | 4 | 546.5679 | 5
330.9972 | 4 | 661.9944 | 6
524.7552 | 5 | 1049.5105 | 8
534.9404 | 5 | 1069.8809 | 8
573.9449 | 5 | 1147.8898 | 8
599.7227 | 5 | 1199.4453 | 8
512.3923 | 5 | 1024.7846 | 8
573.8168 | 5 | 1147.6336 | 8
630.1667 | 5 | 1260.3334 | 8
681.695 | 6 | 1363.39 | 8
242.0702 | 4 | 484.1403 | 5
291.6367 | 4 | 583.2733 | 5
290.4936 | 4 | 580.9873 | 5
350.6693 | 4 | 701.3387 | 6
375.4803 | 4 | 750.9605 | 6
402.5638 | 5 | 805.1276 | 6
427.3855 | 5 | 854.771 | 6
430.0891 | 5 | 860.1783 | 6
453.84 | 5 | 907.68 | 6
360.7205 | 4 | 721.4409 | 6
391.3696 | 4 | 782.7393 | 6
444.5377 | 5 | 889.0754 | 6
455.5928 | 5 | 911.1855 | 6
548.8465 | 5 | 1097.6931 | 8
628.8755 | 5 | 1257.751 | 8
683.4996 | 6 | 1366.9992 | 8
734.2064 | 6 | 1468.4128 | 8
789.7994 | 6 | 1579.5988 | 8
360.84 | 4 | 721.68 | 6
106.8596 | 2.5 | 213.7192 | 3
913.8143 | 6 | 1827.6287 | 10
969.4037 | 8 | 1938.8074 | 10
1015.343 | 8 | 2030.6859 | 10
1051.8577 | 8 | 2103.7154 | 10
1127.0937 | 8 | 2254.1875 | 10
456.5775 | 5 | 913.1549 | 6
508.0798 | 5 | 1016.1596 | 8
534.9443 | 5 | 1069.8887 | 8
568.82 | 5 | 1137.64 | 8
885.0742 | 6 | 1770.1484 | 10
912.6252 | 6 | 1825.2504 | 10
955.0129 | 8 | 1910.0257 | 10
1024.8269 | 8 | 2049.6538 | 10
1116.5838 | 8 | 2233.1676 | 10
466.2681 | 5 | 932.5363 | 6
509.7501 | 5 | 1019.5003 | 8
543.4703 | 5 | 1086.9406 | 8
607.7455 | 5 | 1215.4911 | 8
667.9 | 6 | 1335.8 | 8
732.8 | 6 | 1465.6 | 8
774.6 | 6 | 1549.2 | 8
813.5 | 6 | 1627 | 10
616.3385 | 5 | 1232.6769 | 8
707.5905 | 6 | 1415.1811 | 8
786.8099 | 6 | 1573.6198 | 8
825.5 | 6 | 1651 | 10
756.8 | 6 | 1513.6 | 8
830.5 | 6 | 1661 | 10
873.3 | 6 | 1746.6 | 10
639.1572 | 5 | 1278.3144 | 8
794.9133 | 6 | 1589.8266 | 8
882.342 | 6 | 1764.6841 | 10
935.9263 | 6 | 1871.8526 | 10
1136.2741 | 8 | 2272.5482 | 10
1332.9681 | 8 | 2665.9362 | 12
1528.3535 | 8 | 3056.707 | 12
626.346 | 5 | 1252.6919 | 8
764.9699 | 6 | 1529.9399 | 8
682.0481 | 6 | 1364.0961 | 8
802.7921 | 6 | 1605.5841 | 10
932.9167 | 6 | 1865.8335 | 10
1000.0001 | 8 | 2000.0002 | 10
753.2463 | 6 | 1506.4926 | 8
820.4429 | 6 | 1640.8858 | 10
953.3171 | 8 | 1906.6342 | 10
1029.7585 | 8 | 2059.5169 | 10
1330.3437 | 8 | 2660.6874 | 12
1378.5213 | 8 | 2757.0426 | 12
1467.9509 | 8 | 2935.9018 | 12
844.864 | 6 | 1689.7279 | 10
982.3526 | 8 | 1964.7052 | 10
1104.8611 | 8 | 2209.7222 | 10
1214.4257 | 8 | 2428.8514 | 10
1383.6857 | 8 | 2767.3715 | 12
1551.2098 | 8 | 3102.4196 | 12
1664.6746 | 10 | 3329.3491 | 12
840.7876 | 6 | 1681.5751 | 10
995.4751 | 8 | 1990.9502 | 10
1093.6698 | 8 | 2187.3397 | 10
1144.8546 | 8 | 2289.7092 | 10
1204.5001 | 8 | 2409.0002 | 10
1252.5 | 8 | 2505 | 12
648.3835 | 5 | 1296.767 | 8
820.3589 | 6 | 1640.7178 | 10
941.0352 | 6 | 1882.0704 | 10
1045.3157 | 8 | 2090.6314 | 10
1136.5096 | 8 | 2273.0192 | 10
1235.933 | 8 | 2471.866 | 10
1229.0007 | 8 | 2458.0014 | 10
1303.9328 | 8 | 2607.8655 | 12
1403.874 | 8 | 2807.748 | 12
1484.3188 | 8 | 2968.6376 | 12
1171.9065 | 8 | 2343.8131 | 10
1316.9347 | 8 | 2633.8694 | 12
1454.2378 | 8 | 2908.4756 | 12
1568.7217 | 8 | 3137.4434 | 12
1414.8836 | 8 | 2829.7672 | 12
1523.3743 | 8 | 3046.7486 | 12
1625.1171 | 10 | 3250.2342 | 12
1757.2796 | 10 | 3514.5593 | 12
1846.8509 | 10 | 3693.7017 | 14
1914.581 | 10 | 3829.162 | 14
1634.3829 | 10 | 3268.7658 | 12
1915.2738 | 10 | 3830.5476 | 14
2165.2718 | 10 | 4330.5437 | 16
1914.1469 | 10 | 3828.2938 | 14
2017.9874 | 10 | 4035.9748 | 14
2141.5995 | 10 | 4283.199 | 16
2290.5785 | 10 | 4581.157 | 16
1727.4951 | 10 | 3454.9903 | 12
1826.6982 | 10 | 3653.3965 | 14
2003.3556 | 10 | 4006.7112 | 14
2187.1986 | 10 | 4374.3972 | 16
2293.6739 | 10 | 4587.3477 | 16
2422.2984 | 10 | 4844.5968 | 16
2547.3614 | 12 | 5094.7228 | 16
2953.0528 | 12 | 5906.1056 | 18
3220.9607 | 12 | 6441.9215 | 18
3579.8797 | 14 | 7159.7593 | 20
3926.8748 | 14 | 7853.7497 | 20
4128.2784 | 14 | 8256.5567 | 20